## Credits, worst circuits, storms
RELIABILITY DATA TEMPLATE
Utility: | Consumers Energy Co. |  |  | □ Required Fields
Reporting Month: | 2023-04-30 |  |  | ■ Optional Fields
CUSTOMER CREDITS PROVIDED DURING THE MONTH
Item |  | Sector | Number of Customers Eligible for Credits | Total Customer Credits ($)
Customer Credits Provided for Failure to Restore Service within 96 Hours of the Start of Sustained Interruption during Catastrophic Conditions |  | Residential | 67 | 1675
|  | Commercial | 2 | 6.96
|  | Industrial | 0 | 0
Customer Credits Provided for Failure to Restore Service within 48 Hours of the Start of Sustained Interruption during Gray Sky Conditions |  | Residential | 0 | 0
|  | Commercial | 0 | 0
|  | Industrial | 0 | 0
Customer Credits Provided for Failure to Restore Service within 16 Hours of the Start of Sustained Interruption during Normal Conditions |  | Residential | 562 | 19350
|  | Commercial | 69 | 50.28
|  | Industrial | 2 | 10.06
Customer Credits Provided to Individual Customers Who Experienced 6 or more Sustained Interruptions. |  | Residential | 16 | 450
|  | Commercial | 1 | 35
|  | Industrial | 0 | 0
WORST PERFORMING CIRCUITS DURING THE MONTH AND YEAR
(1) For each electric utility with 1,000,000 or more customers, a list of its 10 worst performing circuits for the prior month in terms of SAIDI and SAIFI. For each listed circuit, provide the following information below.
(2) For each electric utility or cooperative with less than 1,000,000 customers, a list of the worst performing 1% of circuits for the prior month in terms of SAIDI and SAIFI. For each listed circuit, provide the following information below.
SAIDI
Item/Area |  | circuit1 | circuit2 | circuit3 | circuit4 | circuit5 | circuit6 | circuit7 | circuit8 | circuit9 | circuit10
Circuit Name |  | SPRINGPORT | DEVEREAUX | STATE STREET | HOSPITAL | WEISS | BARNARD | BAYSIDE | WARWICK | MACKINAW | ELK RAPIDS
Circuit Number |  | 54201 | 54202 | 21703 | 72301 | 72302 | 72304 | 72303 | 21702 | 21701 | 79802
Circuit Length (miles) |  | 78.94 | 43.86 | 9.58 | 5.06 | 8.98 | 11.37 | 11.12 | 10.96 | 9.32 | 26.24
SAIDI all weather (monthly) | Residential | 1090.1935 | 1079.637 | 484.4912 | 497.4226 | 485.1506 | 370.2474 | 337.3644 | 390.2058 | 379.9625 | 319.1143
| Commercial | 162.7324 | 145.4118 | 36.1475 | 20.7853 | 32.1235 | 146.0794 | 175.9845 | 23.5855 | 20.9554 | 79.8683
| Industrial | 0 | 4.4064 | 0 | 0 | 0 | 0 | 2.9209 | 0 | 0 | 0.28245
| Overall | 1268.2991 | 1236.0648 | 524.7531 | 524.2966 | 521.0533 | 519.6927 | 517.7302 | 414.0899 | 403.008 | 401.5239
Number of Customers Served | Residential | 775 | 569 | 1893 | 1068 | 1506 | 624 | 525 | 1440 | 1640 | 1234
| Commercial | 114 | 73 | 127 | 40 | 95 | 239 | 268 | 94 | 91 | 322
| Industrial | 0 | 2 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 1
Substation Name |  | SPRINGPORT | SPRINGPORT | STATE STREET | BARNARD | BARNARD | BARNARD | BARNARD | STATE STREET | STATE STREET | ANTRIM
Location of Circuit Span - Zip Codes |  | 48827, 49224, 49269, 49284 | 48827, 49284 | 48602, 48603 | 48602 | 48602, 48603 | 48603 | 48603 | 48602, 48603 | 48602, 48603, 48638 | 49629, 49648, 49690
Location of Circuit Span - Census Tracts |  | 26025003200, 26025003700, 26045021100, 26045021202, 26075006500, 26075006600 | 26045021202, 26075006600 | 26145001500, 26145001600, 26145002000, 26145002100, 26145010401 | 26145001800, 26145001900, 26145002000, 26145010401 | 26145001900, 26145002000, 26145002100, 26145010401, 26145010700 | 26145010304, 26145010401 | 26145010304, 26145010401 | 26145002100, 26145010401, 26145010402 | 26145001500, 26145002100, 26145010402 | 26009960600
Last Circuit Trim (year) |  | 2016-06-30 | 2011-06-30 | 2017-06-30 | 2020-06-30 | 2023-06-30 | 2014-06-30 | 2014-06-30 | 2013-06-30 | 2021-06-30 | 2016-06-30
List of Outages and Causes |  | Equipment Failure-99.6%, Public Tree Trimming-0.2%, No Specific Cause Found-0.2% | Equipment Failure-100.0% | Equipment Failure-98.6%, Trees-1.4% | Equipment Failure-99.9%, Weather-0.1% | Equipment Failure-99.8%, No Specific Cause Found-0.2% | Equipment Failure-100.0% | Equipment Failure-100.0% | Equipment Failure-100.0% | Equipment Failure-100.0% | No Specific Cause Found-100.0%, Equipment Failure-0.0%
SAIFI
Item/Area |  | circuit1 | circuit2 | circuit3 | circuit4 | circuit5 | circuit6 | circuit7 | circuit8 | circuit9 | circuit10
Circuit Name |  | OXBOW | PARKER | ADDISON | BONANZA | BURROWS | GRATIOT | ELK RAPIDS | HUBBARD LAKE | STOREY ROAD | RURAL
Circuit Number |  | 123102 | 46501 | 18302 | 43503 | 33902 | 33903 | 79802 | 151601 | 45301 | 37902
Circuit Length (miles) |  | 34.1 | 10.85 | 61.02 | 25.25 | 7.57 | 16.85 | 26.24 | 15.54 | 82.87 | 127.93
SAIFI all weather (monthly) | Residential | 2.3775 | 2.4483 | 1.8916 | 1.7185 | 1.831 | 1.8384 | 1.5222 | 1.5961 | 1.5021 | 1.4599
| Commercial | 0.19608 | 0.12532 | 0.3202 | 0.19417 | 0.08571 | 0.06612 | 0.38089 | 0.15335 | 0.1826 | 0.17719
| Industrial | 0 | 0 | 0.00493 | 0 | 0 | 0 | 0.00135 | 0.00216 | 0 | 0
| Overall | 2.6471 | 2.5788 | 2.2291 | 1.932 | 1.9262 | 1.9164 | 1.9152 | 1.7603 | 1.6933 | 1.6419
Number of Customers Served | Residential | 817 | 708 | 741 | 189 | 998 | 2255 | 1234 | 444 | 1262 | 1025
| Commercial | 90 | 149 | 128 | 23 | 41 | 81 | 322 | 49 | 211 | 136
| Industrial | 0 | 3 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 0
Substation Name |  | BIG PRAIRIE | DIVISION | MANITOU BEACH | LAKE ODESSA | BURROWS | BURROWS | ANTRIM | HUBBARD LAKE | BRICKER | HESPERIA
Location of Circuit Span - Zip Codes |  | 49337, 49349 | 49315, 49508, 49548 | 49220, 49233, 49247, 49249, 49253, 49262, 49271 | 48849, 49325 | 48602, 48638 | 48602, 48638 | 49629, 49648, 49690 | 48705, 48742, 48762 | 48809, 48838, 49331, 49341 | 49309, 49349, 49412, 49421
Location of Circuit Span - Census Tracts |  | 26123970700, 26123970800 | 26081014602, 26081014701, 26081014704, 26081014803, 26081014805 | 26059050100, 26059050600, 26091060401, 26091060402 | 26015010100, 26015010200, 26067031200, 26067031300 | 26145001400, 26145010501, 26145010600 | 26145001300, 26145001400, 26145002100, 26145010402, 26145010501 | 26009960600 | 26001000100, 26001970400, 26001970500 | 26067030300, 26067030400, 26081010802, 26081010902, 26117971100, 26117971300 | 26123970100, 26123970300, 26123970400, 26123970600, 26127010500, 26127010600
Last Circuit Trim (year) |  | 2019-06-30 | 1994-06-30 | 2018-06-30 | 2010-06-30 | 2022-06-30 | 2022-06-30 | 2016-06-30 | 2018-06-30 | 2020-06-30 | 2010-06-30
List of Outages and Causes |  | Trees - Outside ROW-99.8%, Trees-0.1%, Equipment Failure-0.1% | Weather-99.9%, Animal-0.1% | Animal-86.0%, Forced Outage/Emergency-12.2%, No Specific Cause Found-1.5%, Equipment Failure-0.1%, Unique Incident-0.1%, Public Damage-0.1% | Car/Pole Accident-100.0% | No Specific Cause Found-100.0% | No Specific Cause Found-100.0% | No Specific Cause Found-99.9%, Equipment Failure-0.1% | Trees-51.9%, Equipment Failure-48.1% | No Specific Cause Found-63.8%, Equipment Failure-36.1%, Unique Incident-0.1% | Trees-64.2%, Equipment Failure-35.7%, Weather-0.1%
|  | CEMI1 | CEMI2 | CEMI3 | CEMI4 | CEMI5 | CEMI6 | CEMI7 | CEMI8 | CEMI9 | CEMI10
Number of CEMI Reporting for Indices CEMI0 through CEMI10+ (number of customers, monthly) |  | 150219 | 14494 | 1758 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Number of CEMI Reporting for Indices CEMI0 through CEMI10+ (number of customers, year-to-date) |  | 620641 | 207776 | 75241 | 29662 | 10770 | 3493 | 1086 | 520 | 314 | 63
Number of CELID Reporting for Indices: | CELID8hours | CEMI1: 9341
| CELID24hours | CEMI1: 137
| CELID48hours | CEMI1: 0
Number of Non-Residential Customers Experiencing Momentary Interruptions |  | CEMI1: 28278
Storm Outage | Storm #1 | CEMI1: Storm #2; CEMI2: Storm #3; CEMI3: Storm #4; CEMI4: Storm #5
Storm Name
Date Storm Began | 2023-04-01 | CEMI1: 2023-04-05
Date Storm Ended
Storm Type
Customers Interrupted (#) | 10247 | CEMI1: 27116
Storm Duration (hours)
Duration of restoration efforts (hours) | 22 | CEMI1: 14
Date restoration efforts ended | 2023-04-01 | CEMI1: 2023-04-05
spent per event ($) | 1502519 | CEMI1: 2147193
paid in outage credits ($)
Non-baseload resources requested (Y/N)
Company linemen used (#)
contractor workers used (#)
non-baseload workers used (#)
Company crews used (#)
Contractor crews used (#)
Non-baseload crews used (#)
Wire down personnel used (#)
Downed wires
Non-baseload resources cost ($) | 304071 | CEMI1: 507500

## System Reliability Data
RELIABILITY DATA TEMPLATE
Utility: | Consumers Energy Co. |  |  | □ Required Fields
Reporting Month: | 2023-04-30 |  |  | ■ Optional Fields
OVERALL RELIABILITY DATA
| Meter Reading Factor R460.732 (a) | New Service Installation Factor R460.732(b) | Wire Down Relief Factor R460.732 (c) |  | Outage Restoration |  |  |  | CEMI4 | Line Clearing/ Tree Trimming | [5 empty] | Total Customer outages | Outage Causes | [9 empty] | Reliability Metrics (all weather)
[5 empty] | All Conditions R460.732 (d) | Normal Conditions R460.732 (e) | Gray-Sky Conditions R460.732 (f) | Catastrophic Conditions R460.732 (g) | Sustained Interruptions R460.732 (h(i)) | [7 empty] | Equipment | Lightning | Planned | Power Supply | Public | Vegetation | Weather (other than lightning) | Wildlife | Unknown | Other | SAIDI | SAIFI | CAIDI | ASAI | MAIFI
Service Territory as a Whole | Meter Reading Factor (Percentage) | New Services Installed in 15 Business Days or Less (Percentage) | The percentage of the first responder guarded downed wires that are relieved by an electric utility representative within 120 minutes after notification in MSAs. | The percentage of the first responder guarded downed wires that are relieved by an electric utility representative within 180 minutes after notification in non-MSAs. | Percentage of Customers Restored in 36 Hours or Less | Percentage of Customers Restored in 8 Hours or Less | Percentage of Customers Restored in 24 Hours or Less | Percentage of Customers Restored in 48 Hours or Less | Number of Customers Experiencing 4 or More Sustained Interruptions | Amount of Line Cleared (miles) | Capital Spend ($) | O&M Spend ($) | Quarterly Line Clearing Target (miles) | Quarterly Line Clearing Target (% of internal target met) | Cumulative Line Clearing Target (%) | Total Customer outages | Total number of outages causes by equipment failure | Total number of outages caused by lightning | Total number of planned and forced outages | Total number of outages caused by transmission or generation failure | Total number of outages caused by an act of the public at large | Total number of outages caused by trees | Total number of outage caused by weather | Total number of outages caued by animal interference | Total number of outages caused by unknonwn causes | Total number of outages caused by other causes | System Average Interruption Duration Index | System Average Interruption Frequency Index | Customer Average Interruption Duration Index (contribution to total CAIDI) | Average Service Availability Index | Momentary Average Interruption Frequency Index
Service Territory (Month) | 93.8% | 57.8% | 80.9% | 87.7% | 100% | 91.8% | 99.9% |  | 29662 | 492.2678 | 475 | 7850 | 1332.7918 | 36.94% | 67.91% | 166479 | 36069 | 10596 | 19857 | 4278 | 7166 | 42075 | 15248 | 3117 | 19055 | 9018 | 13.82 | 0.08 | 181.67 | 0.9997 | 0.1849
Service Territory (Year to Date) | 93.5% | 48.18% | 50.1% | 61.7% | 83% | 95.3% | 98.2% | 73.3% | 29662 | 1792.3984 | 1638 | 27842 | 2639.2918 | 67.91% | 67.91% | 949597 | 137142 | 11281 | 38039 | 7652 | 54190 | 379590 | 198188 | 9142 | 63179 | 51194 | 497.58 | 0.48 | 1033.97 | 0.9971 | 0.7827
MPSC Annual Performance Standard | 95% or more | 90% or more completed within 15 business days | 90% or more within 120 minutes in MSAs | 90% or more within 180 minutes in non-MSAs | 90% or more customers restored in 36 hours or less | 90% or more customers restored in 8 hours or less | 90% or more customers restored in 24 hours or less | 90% or more customers restored in 48 hours or less | 6% or less before 2030; 5% or less in 2030 or later
For electric utilities with greater than 100,000 customers, please provide a summary of progress toward achieving a targeted line clearing cycle.
See tab "forestryCircuit"

## Circuit
RELIABILITY DATA TEMPLATE
Utility: | Consumers Energy Co. |  |  | □ Required Fields
Reporting Month: | 2023-04-30 |  |  | ■ Optional Fields
RELIABILITY DATA REPORTED BY CIRCUIT
|  | Meter Reading Factor R460.732 (a) | New Service Installation Factor R460.732(b) | Wire Down Relief Factor R460.732 (c) |  | Outage Restoration |  |  |  | CEMI4 | Line Clearing/ Tree Trimming | [5 empty] | Total Customer outages | Outage Causes | [9 empty] | Reliability Metrics (all weather)
[6 empty] | All Conditions R460.732 (d) | Normal Conditions R460.732 (e) | Gray-Sky Conditions R460.732 (f) | Catastrophic Conditions R460.732 (g) | Sustained Interruptions R460.732 (h(i)) | [7 empty] | Equipment | Lightning | Planned | Power Supply | Public | Vegetation | Weather (other than lightning) | Wildlife | Unknown | Other | SAIDI | SAIFI | CAIDI | ASAI | MAIFI
Circuit or Geographical Area | Circuit or Area Name | Meter Reading Factor (Percentage) | New Services Installed in 15 Business Days or Less (Percentage) | The percentage of the first responder guarded downed wires that are relieved by an electric utility representative within 120 minutes after notification in MSAs. | The percentage of the first responder guarded downed wires that are relieved by an electric utility representative within 180 minutes after notification in non-MSAs. | Percentage of Customers Restored in 36 Hours or Less | Percentage of Customers Restored in 8 Hours or Less | Percentage of Customers Restored in 24 Hours or Less | Percentage of Customers Restored in 48 Hours or Less | Number of Customers Experiencing 4 or More Sustained Interruptions | Amount of Line Cleared (miles) | Capital Spend ($) | O&M Spend ($) | Quarterly Line Clearing Target (miles) | Quarterly Line Clearing Target (% of internal target met) | Cumulative Line Clearing Target (%) | Total Customer outages | Total number of outages causes by equipment failure | Total number of outages caused by lightning | Total number of planned and forced outages | Total number of outages caused by transmission or generation failure | Total number of outages caused by an act of the public at large | Total number of outages caused by trees | Total number of outages caused by wind, snow, ice, hail, and rain | Total number of outages caued by animal interference | Total number of outages caused by unknonwn causes | Total number of outages caused by other causes | System Average Interruption Duration Index | System Average Interruption Frequency Index | Customer Average Interruption Duration Index (contribution to total CAIDI) | Average Service Availability Index | Momentary Average Interruption Frequency Index
Circuit | 074404 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.75 | 0.03 | 58.16 | 1 | 0.0151
Circuit | 147202 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.92 | 0 | 192.55 | 1 | 0.1088
Circuit | 156202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 27 | 7 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 8.13 | 0.04 | 185.14 | 0.9998 | 0.0179
Circuit | 116501 |  |  |  |  | 1 | 1 |  |  | 6 | 0 |  |  | 1.43 | 0 | 0.53 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 3.07 | 0.04 | 87.12 | 0.9999 | 0.0059
Circuit | 149402 | [8 empty] | 0 | [21 empty] | 0.2427
Circuit | 080902 |  |  |  |  | 1 |  | 1 |  | 401 | [6 empty] | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0.04 | 63.05 | 0.9999
Circuit | 093602 | [8 empty] | 0
Circuit | 049204 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 0 | 306 | 1 | 0.001
Circuit | 082201 |  |  |  |  | 1 | 1 | 1 |  | 14 | [6 empty] | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 1 | 1 | 0 | 26.76 | 0.1 | 275.68 | 0.9994 | 0.0069
Circuit | 034802 | [8 empty] | 0 | [21 empty] | 0.0015
Circuit | 136804 | [9 empty] | 1.92 |  |  | 3.84 | 0.5 | 0.5
Circuit | 106301
Circuit | 011502
Circuit | 091701 | [8 empty] | 0 | [21 empty] | 0.0108
Circuit | 031301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 184 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 88 | 11.99 | 0.09 | 137.51 | 0.9997 | 0.0104
Circuit | 101202 | [8 empty] | 0
Circuit | 102202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.19 | 0 | 119.86 | 1 | 0.0078
Circuit | 066503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 1 | 0 | 44.32 | 0.2 | 219.49 | 0.999 | 0.0095
Circuit | 087201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 80 | 1
Circuit | 080901 |  |  |  |  | 1 | 1 |  |  | 11 | [6 empty] | 29 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 2 | 1 | 0 | 13.61 | 0.06 | 239.85 | 0.9997 | 0.6301
Circuit | 112101 |  |  |  |  | 1 | 0.944 | 1 |  | 0 | 0 |  |  | 4.63 | 0 | 0 | 37 | 20 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 4.37 | 0.02 | 196.43 | 0.9999 | 0.4675
Circuit | 003802 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 0 | 459.5 | 1 | 0.0046
Circuit | 010204 | [8 empty] | 0 | [21 empty] | 0.0009
Circuit | 029602 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0 | 114.56 | 1 | 0.0029
Circuit | 046302 | [8 empty] | 0 | [6 empty] | 1104 | 0 | 0 | 1104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.9401
Circuit | 130905 | [8 empty] | 0
Circuit | 039301 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.16 | 0 | 143.38 | 1 | 0.0101
Circuit | 033602 |  |  |  | 1 | 1 | 1 | 1 |  | 0 | [6 empty] | 150 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 135 | 0 | 24.36 | 0.21 | 114.8 | 0.9994
Circuit | 018302 |  |  | 0 |  | 1 | 0.998 |  |  | 189 | [6 empty] | 905 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 778 | 14 | 111 | 304.73 | 2.31 | 131.99 | 0.9929 | 1.398
Circuit | 103802 | [8 empty] | 0 | 17.06 |  |  | 8.04 | 2.12 | 1.59 | [15 empty] | 0.0039
Circuit | 090701 |  |  | 1 | [5 empty] | 0
Circuit | 042201 |  |  |  |  | 1 | 1 |  |  | 89 | [6 empty] | 109 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 158.97 | 1.02 | 156.06 | 0.9963 | 0.972
Circuit | 049701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 253 | 137 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 51 | 0 | 51.11 | 0.63 | 81.41 | 0.9988
Circuit | 076603 | [8 empty] | 0 | [21 empty] | 0.0021
Circuit | 074903 | [8 empty] | 0
Circuit | 070601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 86 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 4.04 | 0.09 | 45.71 | 0.9999
Circuit | 168904 |  |  |  |  | 1 | 1 |  |  | 3 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 258 | 1 | 0.0557
Circuit | 073101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 155 | 92 | 0 | 0 | 0 | 0 | 46 | 0 | 17 | 0 | 0 | 6.59 | 0.06 | 110.6 | 0.9998 | 0.0008
Circuit | 090501
Circuit | 051002 | [30 empty] | 0.0031
Circuit | 153602 | [8 empty] | 0
Circuit | 050901 |  |  |  |  | 1 | 1 |  |  | 526 | [6 empty] | 528 | 0 | 0 | 527 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.05 | 0 | 26.49 | 1 | 0.5996
Circuit | 136802 | [9 empty] | 3.16 |  |  | 3.12 | 1.01 | 1.01
Circuit | 127501 | [8 empty] | 0
Circuit | 006602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69 | 0.01 | 116.23 | 1
Circuit | 051101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 249 | 1 | 245 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 25.45 | 0.16 | 163.3 | 0.9994 | 0.8367
Circuit | 136602 |  |  | 1 |  | 1 | 1 |  |  | 10 | 0 |  |  | 0 | 0 | 1 | 839 | 828 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 0 | 161.83 | 1.02 | 159.32 | 0.9963 | 0.0654
Circuit | 070701 | [8 empty] | 0 | [21 empty] | 0.0028
Circuit | 134702 |  |  |  |  | 1 | 0.968 | 1 |  | 1 | 6.43 |  |  | 13.38 | 0.48 | 0.8 | 32 | 2 | 0 | 0 | 0 | 0 | 26 | 3 | 0 | 1 | 0 | 3.05 | 0.02 | 141.39 | 0.9999 | 2.0742
Circuit | 040402 | [8 empty] | 5 | [21 empty] | 0.003
Circuit | 021201 | [8 empty] | 1 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0015
Circuit | 023506 |  |  | 1 | [5 empty] | 0 | [21 empty] | 0.0011
Circuit | 052002 | [8 empty] | 0 | [21 empty] | 0.0052
Circuit | 127701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0.01 | 44.55 | 1 | 0.0306
Circuit | 138302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 8 | 1 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.07 | 0.01 | 166.45 | 1 | 0.0008
Circuit | 165902 |  |  |  |  | 1 |  | 1 |  | 1 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 3.3 | 0.03 | 122.3 | 0.9999 | 0.1124
Circuit | 119102 | [8 empty] | 103 | [21 empty] | 0.0031
Circuit | 060702 | [8 empty] | 0 | [21 empty] | 0.0007
Circuit | 103101 | [30 empty] | 0.0092
Circuit | 025701 |  |  |  |  | 1 | 1 |  |  | 93 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.13 | 0 | 136 | 1 | 0.9663
Circuit | 081804 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 36 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 7.16 | 0.06 | 127.55 | 0.9998 | 0.0796
Circuit | 087701
Circuit | 074601 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.04 | 0 | 59.79 | 1
Circuit | 078901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 156 | 82 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 44.87 | 0.5 | 89.17 | 0.999 | 0.0258
Circuit | 048204 |  |  |  | 1 | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0 | 515.88 | 1 | 0.0009
Circuit | 126701 | [8 empty] | 0 | [21 empty] | 0.6918
Circuit | 006403 | [8 empty] | 1 | [21 empty] | 0.0525
Circuit | 166302
Circuit | 039303 |  |  | 0 |  | 1 | 0.373 |  |  | 0 | [6 empty] | 83 | 16 | 0 | 0 | 0 | 0 | 41 | 26 | 0 | 0 | 0 | 32.74 | 0.07 | 468.67 | 0.9992 | 0.0067
Circuit | 122602 | [8 empty] | 1 | [21 empty] | 0.0018
Circuit | 076201 | [8 empty] | 15
Circuit | 049203 | [8 empty] | 0 | [6 empty] | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.2604
Circuit | 053302 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.58 | 0 | 1075 | 1 | 0.0022
Circuit | 071702 |  |  |  |  | 1 | 1 | 1 |  | 0 | 1.33 |  |  | 0 | 1 | 3.33 | 100 | 50 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 19.88 | 0.07 | 276.73 | 0.9995 | 0.0036
Circuit | 076003
Circuit | 128404 | [8 empty] | 0 | [21 empty] | 0.0006
Circuit | 081501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 1 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.41 | 0 | 131.62 | 1 | 0.0125
Circuit | 044006 | [30 empty] | 0.0714
Circuit | 062002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.71 | 0 | 172.65 | 1
Circuit | 020903 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.19 | 0 | 166.94 | 1 | 0.1517
Circuit | 148001 | [30 empty] | 0.0036
Circuit | 032101 | [8 empty] | 0 | [21 empty] | 0.9872
Circuit | 167902 |  |  |  | 1 | 1 | 1 | 1 |  | 18 | [6 empty] | 2040 | 2039 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215.76 | 1.01 | 212.69 | 0.995 | 0.0935
Circuit | 102501 |  |  |  |  | 1 | 1 |  |  | 43 | 0 |  |  | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.15 | 0 | 83 | 1 | 0.3095
Circuit | 110401 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 3 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.93 | 0 | 260.15 | 1 | 0.0024
Circuit | 070602 | [9 empty] | 0 |  |  | 4.35 | 0 | 0
Circuit | 059502 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0 | 376 | 1 | 0.0015
Circuit | 036402 | [8 empty] | 0 | [21 empty] | 0.0027
Circuit | 010602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 151.7 | 1 | 0.0205
Circuit | 033302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.81 | 0.01 | 118.06 | 1 | 0.0055
Circuit | 005502 |  |  | 1 | [5 empty] | 0 | [21 empty] | 0.0007
Circuit | 008204 |  |  |  |  | 1 | 1 |  |  | 0 | 3.43 |  |  | 16.35 | 0.21 | 0.25 | 31 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 4.68 | 0.04 | 126.37 | 0.9999 | 0.0012
Circuit | 081504 |  |  |  |  | 1 | 1 | 1 |  | 0 | 0 |  |  | 0 | 0 | 1 | 423 | 1 | 39 | 382 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4.06 | 0.02 | 204.61 | 0.9999 | 0.1122
Circuit | 111901 |  |  | 1 |  | 1 |  | 1 |  | 496 | [6 empty] | 457 | 0 | 0 | 1 | 0 | 0 | 0 | 456 | 0 | 0 | 0 | 51.08 | 0.4 | 128.03 | 0.9988 | 0.6702
Circuit | 029202 | [8 empty] | 19 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0053
Circuit | 052301
Circuit | 053803 | [30 empty] | 0.1889
Circuit | 138301 |  |  |  |  | 1 | 0.667 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 3.59 | 0.01 | 341.13 | 0.9999 | 0.9228
Circuit | 017503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.94 | 0 | 300.8 | 1 | 0.0047
Circuit | 123601 |  |  | 1 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 58 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 56 | 4.36 | 0.15 | 29.82 | 0.9999 | 0.0076
Circuit | 018201 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1.56 | 0 | 638 | 1
Circuit | 114502 | [8 empty] | 0 | [21 empty] | 0.0023
Circuit | 068602 | [8 empty] | 0 | [21 empty] | 0.016
Circuit | 004802 | [8 empty] | 0
Circuit | 056602 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1.94 | 0 | 892 | 1
Circuit | 021603 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 168 | 0 | 41 | 11 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 31.78 | 0.13 | 243.92 | 0.9993 | 0.0656
Circuit | 148602 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 225 | 1 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 20.62 | 0.15 | 133.22 | 0.9995 | 0.1135
Circuit | 048701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.89 | 0 | 251 | 1
Circuit | 028802 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0 | 271 | 1 | 0.0025
Circuit | 039004 | [8 empty] | 0 | [21 empty] | 0.0074
Circuit | 031101 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 187 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 9.89 | 0.08 | 127.25 | 0.9998 | 0.0025
Circuit | 082001 | [8 empty] | 0 | [21 empty] | 0.0008
Circuit | 113601 | [8 empty] | 0 | 0.3 |  |  | 0 | 1 | 1 | [15 empty] | 0.0012
Circuit | 118401 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1.15 | 0 | 400 | 1 | 0.0029
Circuit | 151002 |  |  |  |  | 1 | 1 |  |  | 528 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.36 | 0 | 215.39 | 1 | 0.0297
Circuit | 040102 |  |  |  |  | 1 |  | 1 |  | 32 | [6 empty] | 6 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.01 | 117.68 | 1 | 0.0011
Circuit | 066602 | [8 empty] | 0 | [21 empty] | 0.0016
Circuit | 017601 | [8 empty] | 0
Circuit | 136806
Circuit | 107701 | [8 empty] | 0 | [21 empty] | 0.9697
Circuit | 072304 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 772 | 772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 519.69 | 1.01 | 517 | 0.988 | 1.0247
Circuit | 011401 |  |  |  |  | 1 | 1 | 1 |  | 40 | [6 empty] | 204 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 54.27 | 0.43 | 126.63 | 0.9987 | 1.6029
Circuit | 160201 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.82 | 0 | 573 | 1 | 0.0115
Circuit | 149501 |  |  | 1 |  | 1 | 1 | 1 |  | 1 | [6 empty] | 15 | 6 | 0 | 0 | 0 | 1 | 8 | 0 | 0 | 0 | 0 | 1.5 | 0.01 | 134.99 | 1 | 0.0044
Circuit | 079801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1042 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1040 | 0 | 209.65 | 1 | 209.25 | 0.9951 | 0.026
Circuit | 073301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.05 | 0 | 57 | 1 | 0.0043
Circuit | 041401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.07 | 0 | 60.93 | 1 | 0.026
Circuit | 034803 | [8 empty] | 0 | [21 empty] | 0.2958
Circuit | 043303
Circuit | 111804 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 1.51 | 0.01 | 127.37 | 1 | 0.0638
Circuit | 137002 | [8 empty] | 0 | [21 empty] | 0.0021
Circuit | 162202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 83 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 13.64 | 0.14 | 98.91 | 0.9997 | 0.0166
Circuit | 072303 |  |  |  |  | 1 | 0 |  |  | 3 | [6 empty] | 709 | 709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518.46 | 1 | 517 | 0.988 | 0.8982
Circuit | 075102 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 0 | [15 empty] | 0.0051
Circuit | 006106
Circuit | 030401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.12 | 0 | 100.55 | 1 | 0.0012
Circuit | 079704 | [8 empty] | 0 | [21 empty] | 0.1416
Circuit | 082402 | [8 empty] | 0 | 0 |  |  | 10 | 0 | 0
Circuit | 047501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.08 | 0 | 63.63 | 1
Circuit | 025202 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0.36 | 0 | 221 | 1 | 0.0717
Circuit | 156302 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.29 | 0 | 182 | 1
Circuit | 156401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.56 | 0.01 | 86.64 | 1
Circuit | 081602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0 | 437.08 | 1 | 0.0167
Circuit | 083801 |  |  |  | 1 |  |  |  |  | 7 | [21 empty] | 0.0193
Circuit | 030301 |  |  | 1 |  | 1 | 1 |  |  | 0 | 9.42 |  |  | 30.2 | 0.31 | 0.33 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.08 | 0 | 50 | 1 | 0.0033
Circuit | 067302 | [8 empty] | 0 | [21 empty] | 0.0042
Circuit | 022404 | [8 empty] | 0
Circuit | 057701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 0 | 244 | 1 | 0.793
Circuit | 012002 | [8 empty] | 0 | [21 empty] | 1.023
Circuit | 131401 |  |  |  |  | 1 | 0 |  |  | 0 | 4.28 |  |  | 8.02 | 0.53 | 0.69 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 47.29 | 0.03 | 1437.74 | 0.9989 | 0.9211
Circuit | 111802
Circuit | 065404 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0081
Circuit | 090807 | [30 empty] | 0.2045
Circuit | 001101 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0.48 | 0.02 | 25.27 | 1 | 0.0016
Circuit | 142701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 32 | 1 | 0 | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.21 | 0 | 124.24 | 1 | 0.006
Circuit | 110402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 4 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0.95 | 0.01 | 142.52 | 1 | 0.0193
Circuit | 063702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0.14 | 0.02 | 8.13 | 1 | 0.0008
Circuit | 035101 | [8 empty] | 0 | 0 |  |  | 19.16 | 0 | 0 | [15 empty] | 0.105
Circuit | 093401 | [8 empty] | 0
Circuit | 001903 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Circuit | 107502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2225 | 30 | 0 | 0 | 0 | 0 | 2193 | 0 | 0 | 2 | 0 | 171.87 | 0.76 | 227.18 | 0.996 | 1.964
Circuit | 048902 | [8 empty] | 0
Circuit | 148002 |  |  | 1 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 443 | 3 | 0 | 0 | 0 | 434 | 3 | 3 | 0 | 0 | 0 | 83.43 | 0.76 | 109.6 | 0.9981 | 0.2457
Circuit | 003506 | [30 empty] | 0.0022
Circuit | 072602 |  |  |  |  | 1 | 1 |  |  | 0 | 0.22 |  |  | 0.22 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4.56 | 0.03 | 141.27 | 0.9999 | 3.9355
Circuit | 030901 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 82 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 163.83 | 0.17 | 961 | 0.9962 | 0.4116
Circuit | 006802 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 114 | 0 | 0 | 0 | 0 | 0 | 44 | 70 | 0 | 0 | 0 | 16.46 | 0.12 | 135.76 | 0.9996 | 0.0149
Circuit | 050201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1653 | 0 | 0 | 0 | 0 | 1653 | 0 | 0 | 0 | 0 | 0 | 113.13 | 1 | 113.19 | 0.9974 | 0.0151
Circuit | 019202 |  |  |  |  | 1 | 1 |  |  | 8 | [6 empty] | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 0.03 | 66.77 | 1 | 0.2051
Circuit | 123101 |  |  |  |  | 1 | 1 |  |  | 14 | [6 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 5.46 | 0.03 | 213.57 | 0.9999
Circuit | 118301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 95 | 58 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 45.13 | 0.39 | 116.86 | 0.999 | 0.0203
Circuit | 002501
Circuit | 005801 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 0.01 | 498.73 | 0.9999 | 0.0081
Circuit | 154903 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 378 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 45.38 | 0.59 | 77.55 | 0.9989 | 0.2136
Circuit | 151202 | [8 empty] | 0 | [21 empty] | 0.0004
Circuit | 042602 |  |  |  |  | 1 | 0.986 |  |  | 1349 | [6 empty] | 72 | 45 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 7.84 | 0.04 | 176.86 | 0.9998 | 0.0431
Circuit | 125604 |  |  |  |  | 1 | 0.718 |  |  | 0 | [6 empty] | 547 | 1 | 0 | 0 | 0 | 546 | 0 | 0 | 0 | 0 | 0 | 105.65 | 0.43 | 248.39 | 0.9976 | 0.4806
Circuit | 004703 |  |  |  |  | 1 | 0.75 |  |  | 0 | [6 empty] | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 1.39 | 0 | 383.25 | 1 | 0.2409
Circuit | 049206 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 59 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 58 | 0 | 0 | 1.56 | 0.04 | 43.69 | 1 | 0.006
Circuit | 061902 | [8 empty] | 0
Circuit | 090301 | [8 empty] | 0 | 0 |  |  | 2.89 | 0 | 0
Circuit | 034202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 39 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 10.29 | 0.03 | 301.29 | 0.9998 | 0.0123
Circuit | 126302 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 2027 | 7 | 1 | 0 | 0 | 0 | 2016 | 0 | 0 | 2 | 1 | 189 | 1.27 | 148.54 | 0.9956 | 0.7087
Circuit | 060204 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.45 | 0 | 112.82 | 1 | 0.4661
Circuit | 008801 |  |  |  |  | 1 |  | 1 |  | 0 | 0 |  |  | 0 | 0 | 1 | 42 | 0 | 0 | 1 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 4.24 | 0.02 | 181.93 | 0.9999 | 0.1621
Circuit | 001102 | [8 empty] | 0
Circuit | 022702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 65 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 62 | 7.89 | 0.09 | 90.28 | 0.9998 | 0.0242
Circuit | 056802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0.32 | 0 | 195 | 1 | 0.7178
Circuit | 006601 |  |  |  |  | 1 |  | 1 |  | 0 | 0 |  |  | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0 | 103 | 1 | 0.6228
Circuit | 070603 | [8 empty] | 0 | [21 empty] | 0.0555
Circuit | 100601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 69.99 | 1 | 0.0025
Circuit | 064801 | [8 empty] | 0 | 0 |  |  | 16.93 | 0 | 0 | [15 empty] | 0.7187
Circuit | 057101 |  |  | 0.5 |  | 1 | 1 |  |  | 3 | [6 empty] | 36 | 1 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 0 | 0 | 10.06 | 0.05 | 204.83 | 0.9998 | 0.9864
Circuit | 138102 |  |  | 1 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 2.42 | 0 | 491.5 | 0.9999 | 0.0168
Circuit | 011003 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0 | 238.03 | 1 | 0.0119
Circuit | 043503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 199 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 352.37 | 2.01 | 175.3 | 0.9918 | 0.6465
Circuit | 003503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.05 | 0 | 77 | 1 | 0.0006
Circuit | 102701 | [8 empty] | 0 | [21 empty] | 0.0007
Circuit | 100802 |  |  |  | 1 | 1 | 1 |  |  | 101 | [6 empty] | 1096 | 0 | 0 | 0 | 0 | 0 | 1096 | 0 | 0 | 0 | 0 | 82.41 | 0.79 | 103.99 | 0.9981 | 2.2878
Circuit | 063203 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.33 | 0 | 80.27 | 1
Circuit | 091602 | [8 empty] | 0 | [21 empty] | 0.0026
Circuit | 106101 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.58 | 0 | 193 | 1
Circuit | 122101 |  |  |  | 1 | 1 | 1 |  |  | 26 | [6 empty] | 258 | 0 | 0 | 1 | 0 | 0 | 256 | 0 | 0 | 1 | 0 | 23.21 | 0.23 | 102.95 | 0.9995 | 0.5333
Circuit | 030101 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 597 | 1 | 0.028
Circuit | 052601 | [8 empty] | 0 | [21 empty] | 0.0062
Circuit | 047302 | [8 empty] | 0 | [21 empty] | 3.0685
Circuit | 084101 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 0 | 423 | 1 | 0.0162
Circuit | 098202 | [8 empty] | 0
Circuit | 040201 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.96 | 0 | 436.29 | 1
Circuit | 115903 |  |  | 0 |  | 1 | 1 |  |  | 0 | [6 empty] | 290 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 32.81 | 0.15 | 215.86 | 0.9992 | 1.1944
Circuit | 123302 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 13 | 2 | 1 | 0 | 0 | 0 | 4 | 5 | 0 | 1 | 0 | 14.41 | 0.04 | 336.9 | 0.9997 | 2.8125
Circuit | 027804 |  |  |  |  | 1 | 0.833 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 1 | 2.24 | 0 | 456.07 | 0.9999 | 0.0098
Circuit | 159201 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.93 | 0.01 | 428.61 | 0.9999
Circuit | 060601 |  |  |  |  | 1 | 1 | 1 |  | 222 | 6.38 |  |  | 29.78 | 0.21 | 0.56 | 798 | 0 | 353 | 0 | 0 | 0 | 442 | 0 | 0 | 3 | 0 | 98.28 | 0.5 | 195.09 | 0.9977 | 0.4097
Circuit | 109502 | [8 empty] | 0 | [21 empty] | 0.0008
Circuit | 124202 | [8 empty] | 0
Circuit | 095305 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0 | 282.71 | 1 | 0.2443
Circuit | 029402 | [8 empty] | 0
Circuit | 021401
Circuit | 025601 | [8 empty] | 0 | [21 empty] | 0.0069
Circuit | 077404
Circuit | 050501 |  |  | 0 |  | 1 | 1 |  |  | 0 | [6 empty] | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.21 | 0.08 | 367.44 | 0.9993 | 5.6624
Circuit | 018901 | [8 empty] | 0
Circuit | 074302 | [8 empty] | 0 | [21 empty] | 0.0031
Circuit | 013403 |  |  |  |  | 1 | 0.955 |  |  | 58 | 0 |  |  | 24.16 | 0 | 0 | 246 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.53 | 0.12 | 141.84 | 0.9996 | 0.0131
Circuit | 000202 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 0.89 | 58 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 1.8 | 0.03 | 65.69 | 1 | 0.0477
Circuit | 011001 |  |  |  | 1 | 1 | 1 | 1 |  | 0 | [6 empty] | 108 | 101 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5 | 8.67 | 0.08 | 109.61 | 0.9998 | 0.0337
Circuit | 027501 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0006
Circuit | 104406 | [8 empty] | 0 | [21 empty] | 0.0015
Circuit | 090504
Circuit | 079002 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1585 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 8 | 1177 | 0 | 138.53 | 1.08 | 128.74 | 0.9968 | 0.2254
Circuit | 132201 |  |  |  |  | 1 | 1 |  |  | 0 | 0.03 |  |  | 0 | 1 | 0.93 | 43 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.27 | 0 | 212 | 1 | 0.005
Circuit | 169303 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2 | 0 | 0 | 1.13 | 0.01 | 129.59 | 1 | 0.5866
Circuit | 062402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 302 | 1 | 0.0015
Circuit | 036804 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 352 | 122 | 0 | 0 | 0 | 1 | 229 | 0 | 0 | 0 | 0 | 18 | 0.15 | 121.42 | 0.9996 | 0.2257
Circuit | 107602 | [30 empty] | 1.8421
Circuit | 092101 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.85 | 0.06 | 193.71 | 0.9997 | 0.0216
Circuit | 000401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45 | 0 | 233 | 1 | 0.3132
Circuit | 061602 |  |  | 1 |  | 1 | 1 |  |  | 4 | [6 empty] | 47 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 12.65 | 0.09 | 135.64 | 0.9997 | 0.002
Circuit | 070402 | [8 empty] | 0 | 0 |  |  | 6 | 0 | 0
Circuit | 115301 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 112 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 25.68 | 0.2 | 131.17 | 0.9994 | 0.014
Circuit | 054404 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 371 | 40 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 13 | 0 | 33.2 | 0.24 | 139.51 | 0.9992 | 0.7999
Circuit | 101801
Circuit | 093603 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 26 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 32.83 | 0.06 | 577.13 | 0.9992
Circuit | 168701 | [9 empty] | 0 |  |  | 4.45 | 0 | 0
Circuit | 063002 |  |  | 0 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 21 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 2 | 0 | 8.92 | 0.05 | 186.1 | 0.9998 | 0.9452
Circuit | 042101 |  |  |  |  | 1 | 1 |  |  | 43 | [6 empty] | 34 | 1 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 1.01 | 0.05 | 22.01 | 1 | 0.0243
Circuit | 019403 | [8 empty] | 0 | [21 empty] | 0.0012
Circuit | 139502 |  |  | 1 |  | 1 | 1 | 1 |  | 2 | [6 empty] | 55 | 1 | 1 | 0 | 0 | 0 | 52 | 0 | 1 | 0 | 0 | 5.3 | 0.03 | 157.14 | 0.9999 | 0.0018
Circuit | 036905
Circuit | 053301 |  |  |  |  | 1 | 0.8 |  |  | 0 | [6 empty] | 5 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2.78 | 0.01 | 398.39 | 0.9999 | 0.8047
Circuit | 072701 | [8 empty] | 0 | [21 empty] | 0.0032
Circuit | 025501 |  |  | 1 |  | 1 |  | 0.953 |  | 0 | [6 empty] | 406 | 36 | 0 | 0 | 0 | 0 | 326 | 44 | 0 | 0 | 0 | 158.26 | 0.62 | 253.77 | 0.9963 | 0.0108
Circuit | 033902 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 809 | 0 | 282.26 | 1.99 | 142 | 0.9935 | 0.113
Circuit | 048001 |  |  |  |  | 1 | 0.974 |  |  | 0 | [6 empty] | 422 | 0 | 0 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 0 | 71.11 | 0.33 | 215.03 | 0.9984 | 0.0933
Circuit | 035702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.92 | 0 | 232.53 | 1
Circuit | 088501 |  |  |  |  | 1 | 0.833 | 1 |  | 103 | [6 empty] | 27 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 21 | 0 | 5.74 | 0.02 | 311.02 | 0.9999 | 0.015
Circuit | 158701 |  |  |  |  | 1 | 1 |  |  | 130 | [6 empty] | 265 | 1 | 0 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 0 | 40.03 | 1.02 | 39.42 | 0.9991 | 0.2797
Circuit | 023505 |  |  |  |  | 1 | 0 |  |  | 0 | 0 |  |  | 1 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1.39 | 0 | 651 | 1 | 0.0043
Circuit | 151401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0.11 | 175.99 | 0.9996 | 0.0672
Circuit | 006705 |  |  |  |  | 1 | 0.333 |  |  | 0 | 0.07 |  |  | 0 | 1 | 1.02 | 32 | 2 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2.92 | 0 | 709.83 | 0.9999 | 0.9671
Circuit | 001301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.23 | 0 | 250 | 1 | 0.7428
Circuit | 114202 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0113
Circuit | 079201 |  |  |  |  | 1 | 1 | 1 |  | 0 | 0 |  |  | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 1 | 4.88 | 0.05 | 102.66 | 0.9999 | 0.0008
Circuit | 150603 | [9 empty] | 0 |  |  | 18 | 0 | 0
Circuit | 073501 | [8 empty] | 0 | [21 empty] | 0.0032
Circuit | 040802 | [8 empty] | 0 | 0 |  |  | 2.5 | 0 | 0 | [15 empty] | 0.1132
Circuit | 022302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.87 | 0.02 | 93.43 | 1 | 0.1888
Circuit | 010002
Circuit | 053401 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 46 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8.74 | 0.08 | 113.61 | 0.9998 | 0.0033
Circuit | 058902 |  |  |  |  | 1 | 0.8 |  |  | 0 | [6 empty] | 957 | 5 | 0 | 952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.78 | 0.01 | 339.75 | 1 | 0.0074
Circuit | 010404 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1.1 | 0 | 223.25 | 1 | 0.0875
Circuit | 034604 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0 | 99.14 | 1
Circuit | 067702 | [8 empty] | 0 | [21 empty] | 0.0039
Circuit | 100801 | [8 empty] | 0
Circuit | 140202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.12 | 0 | 55 | 1 | 0.0084
Circuit | 112102 |  |  |  | 0 | 1 | 1 | 1 |  | 0 | [6 empty] | 4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0.72 | 0 | 153.64 | 1 | 0.0047
Circuit | 087202 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 123 | 3 | 0 | 1 | 0 | 0 | 59 | 59 | 0 | 1 | 0 | 32.71 | 0.1 | 343.46 | 0.9992 | 0.0008
Circuit | 051402 |  |  |  |  | 1 | 1 |  |  | 615 | 0 |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.07 | 0 | 61 | 1 | 0.0011
Circuit | 037501 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.12 | 0 | 93.49 | 1 | 0.0039
Circuit | 070703
Circuit | 002301
Circuit | 151502 | [8 empty] | 0 | [21 empty] | 0.0081
Circuit | 014104 | [9 empty] | 6.15 |  |  | 15.86 | 0.39 | 0.58
Circuit | 023802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 220 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 8.63 | 0.18 | 48.76 | 0.9998 | 0.3009
Circuit | 104201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.29 | 0 | 139 | 1 | 0.0222
Circuit | 099104 | [30 empty] | 0.8635
Circuit | 082502 |  |  |  |  | 1 | 0.8 | 1 |  | 0 | [6 empty] | 21 | 0 | 0 | 0 | 0 | 0 | 20 | 1 | 0 | 0 | 0 | 33.5 | 0.19 | 178.65 | 0.9992 | 0.3393
Circuit | 040101 | [8 empty] | 0 | [21 empty] | 1.5408
Circuit | 034602 | [8 empty] | 0 | [6 empty] | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.3227
Circuit | 026801 | [8 empty] | 0 | [21 empty] | 0.0042
Circuit | 030102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.18 | 0 | 98 | 1
Circuit | 076605 | [8 empty] | 0
Circuit | 024401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.05 | 0 | 34 | 1 | 0.0126
Circuit | 045402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0.42 | 0.01 | 54.48 | 1 | 0.0021
Circuit | 019404 | [8 empty] | 0 | [21 empty] | 0.2936
Circuit | 029302
Circuit | 066802 | [8 empty] | 0
Circuit | 044801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 67 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 66 | 0 | 4.94 | 0.06 | 84.86 | 0.9999 | 0.0174
Circuit | 035201 | [8 empty] | 0 | 0 |  |  | 0.61 | 0 | 0 | [15 empty] | 8.084
Circuit | 058301 | [30 empty] | 0.0038
Circuit | 112602 | [8 empty] | 0 | [21 empty] | 0.0008
Circuit | 148201 | [9 empty] | 0 |  |  | 0 | 0 | 1
Circuit | 112202 |  |  |  |  | 1 | 1 | 1 |  | 516 | 5.41 |  |  | 6.7 | 0.81 | 0.84 | 65 | 0 | 0 | 0 | 0 | 0 | 48 | 15 | 2 | 0 | 0 | 9.21 | 0.04 | 241.98 | 0.9998 | 0.1043
Circuit | 067602 | [8 empty] | 0
Circuit | 064706 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.02 | 0 | 29 | 1 | 0.0067
Circuit | 111902 |  |  |  |  | 1 |  | 1 |  | 24 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 4 | 0.02 | 217.82 | 0.9999 | 0.0985
Circuit | 107703 | [8 empty] | 0 | [21 empty] | 0.9697
Circuit | 057801 |  |  |  |  | 1 | 0.988 |  |  | 55 | 0 |  |  | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 749 | 0 | 0 | 0 | 7 | 267.25 | 0.77 | 347.15 | 0.9938 | 0.4847
Circuit | 025401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.32 | 0 | 173 | 1 | 0.0018
Circuit | 129302 | [8 empty] | 0
Circuit | 010403 |  |  |  |  | 1 | 1 | 1 |  | 67 | [6 empty] | 67 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 7.42 | 0.08 | 97.22 | 0.9998 | 0.0991
Circuit | 112001 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 121 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.48 | 0.12 | 99.79 | 0.9997 | 1.8565
Circuit | 115502 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 868 | 181 | 0 | 1 | 0 | 0 | 670 | 16 | 0 | 0 | 0 | 123.78 | 0.67 | 185.45 | 0.9971 | 0.8091
Circuit | 148301 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 22.97 | 0.17 | 132.89 | 0.9995 | 0.4994
Circuit | 020103 | [8 empty] | 0 | [21 empty] | 0.0336
Circuit | 100301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 176 | 44 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 1 | 0 | 22.49 | 0.21 | 108.22 | 0.9995 | 0.0685
Circuit | 101802 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 18.37 | 0.26 | 71 | 0.9996 | 0.0095
Circuit | 109102 |  |  |  |  | 1 | 0.083 |  |  | 2 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 1 | 0 | 9.82 | 0.01 | 688.96 | 0.9998 | 0.0321
Circuit | 130904
Circuit | 009103
Circuit | 049402 |  |  | 0 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0.2 | 0 | 104.66 | 1 | 1.9724
Circuit | 099601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1.39 | 0.01 | 270.27 | 1 | 0.0026
Circuit | 054302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.33 | 0 | 353 | 1 | 0.0009
Circuit | 026002 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 2.98 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 203 | 1 | 0.008
Circuit | 003501 | [8 empty] | 0 | [21 empty] | 0.0039
Circuit | 066904
Circuit | 046902 | [9 empty] | 0 |  |  | 0 | 0 | 0 | [15 empty] | 0.0213
Circuit | 014602 | [8 empty] | 2 | [21 empty] | 0.0009
Circuit | 090303 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 223 | 0 | 0 | 0 | 0 | 0 | 36 | 175 | 7 | 0 | 5 | 34.34 | 0.19 | 177.53 | 0.9992 | 0.5577
Circuit | 001402 | [8 empty] | 0
Circuit | 109302 | [30 empty] | 0.0388
Circuit | 000302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 45 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 10.72 | 0.12 | 91.5 | 0.9998 | 0.0052
Circuit | 008507 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 19 | 1 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0.47 | 0.02 | 28.83 | 1 | 0.0155
Circuit | 071701 | [8 empty] | 0
Circuit | 049601 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0 | 101 | 1 | 0.0034
Circuit | 100501 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.85 | 0.01 | 159.16 | 1 | 1.9016
Circuit | 130901 | [30 empty] | 0.1111
Circuit | 049302 | [8 empty] | 0 | [21 empty] | 0.9561
Circuit | 041702 | [8 empty] | 95
Circuit | 124701 |  |  |  |  | 1 | 1 | 1 |  | 0 | 10.44 |  |  | 10.46 | 1 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 6.69 | 0.02 | 389.91 | 0.9998 | 0.103
Circuit | 036801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.04 | 0 | 55.1 | 1
Circuit | 041103 | [30 empty] | 0.0016
Circuit | 055701
Circuit | 123602 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.52 | 0 | 542 | 0.9999
Circuit | 010701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0.34 | 0 | 175.39 | 1
Circuit | 006603 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1.45 | 0.01 | 136.3 | 1 | 0.0013
Circuit | 009202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 1.67 | 0.01 | 116.58 | 1 | 0.9901
Circuit | 049902 |  |  |  |  | 1 | 0.984 |  |  | 0 | 13.14 |  |  | 19.29 | 0.68 | 0.95 | 189 | 2 | 0 | 0 | 0 | 0 | 138 | 0 | 1 | 0 | 48 | 39.62 | 0.13 | 314.48 | 0.9991 | 0.002
Circuit | 050401 |  |  |  |  | 1 | 0 | 1 |  | 0 | [6 empty] | 6 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.55 | 0.01 | 247.35 | 1 | 1.0031
Circuit | 058801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.75 | 0.01 | 333.15 | 1 | 0.0026
Circuit | 008802 |  |  |  |  | 1 | 1 |  |  | 80 | [6 empty] | 575 | 250 | 0 | 0 | 0 | 0 | 300 | 24 | 0 | 1 | 0 | 81.15 | 0.51 | 158.62 | 0.9981 | 0.2509
Circuit | 018501 |  |  |  |  | 1 | 0 |  |  | 2 | 0 |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.58 | 0 | 718 | 1 | 0.9715
Circuit | 025203 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 11.58 | 0.09 | 124.25 | 0.9997 | 0.1738
Circuit | 052303 | [8 empty] | 0
Circuit | 160202 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 5 | 1 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.42 | 0 | 98.63 | 1 | 0.123
Circuit | 095302 | [30 empty] | 0.0037
Circuit | 115302 |  |  |  |  | 1 | 1 | 1 |  | 132 | [6 empty] | 77 | 0 | 0 | 0 | 0 | 0 | 75 | 2 | 0 | 0 | 0 | 66.69 | 0.18 | 370.69 | 0.9985 | 0.3107
Circuit | 133901 | [8 empty] | 0 | [21 empty] | 0.0024
Circuit | 042601 |  |  |  |  | 1 | 0.889 |  |  | 52 | [6 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8 | 0 | 2.57 | 0.01 | 228.55 | 0.9999 | 0.8764
Circuit | Circuit Group 1 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9008 | 2789 | 0 | 0 | 3935 | 0 | 2269 | 3 | 0 | 9 | 3 | 1165.48 | 6.33 | 184.06 | 0.973 | 0.3383
Circuit | 041201 |  |  |  |  | 1 | 1 |  |  | 284 | [6 empty] | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1.98 | 0.01 | 136.4 | 1 | 0.0193
Circuit | 014801 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.21 | 0 | 176 | 1 | 0.0152
Circuit | 042902 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.49 | 0 | 361.16 | 1 | 0.1248
Circuit | 007402 |  |  | 1 | 1 | 1 | 0.997 |  |  | 1 | [6 empty] | 300 | 1 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 79.76 | 0.48 | 166.96 | 0.9982 | 0.414
Circuit | 020701 | [8 empty] | 0 | [6 empty] | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0027
Circuit | 050801 | [8 empty] | 0 | [21 empty] | 0.0148
Circuit | 051401 | [8 empty] | 3 | [21 empty] | 1.0522
Circuit | 002601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 323.52 | 1 | 0.001
Circuit | 066905 | [8 empty] | 0
Circuit | 010912 | [30 empty] | 0.0038
Circuit | 054602 | [8 empty] | 0 | [21 empty] | 0.0008
Circuit | 144302
Circuit | 064402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.17 | 0 | 255.29 | 1 | 0.4276
Circuit | 133502 | [8 empty] | 0
Circuit | 055104 |  |  |  |  | 1 | 0.021 |  |  | 0 | 0.65 |  |  | 0 | 131.56 | 1.06 | 96 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 92 | 97.65 | 0.06 | 1648.6 | 0.9977 | 0.0025
Circuit | 018002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 4.92 | 0.02 | 216 | 0.9999 | 0.1225
Circuit | 128001 |  |  |  |  | 1 | 1 |  |  | 18 | [6 empty] | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.73 | 0.02 | 71.94 | 1
Circuit | 053101 | [8 empty] | 0 | [21 empty] | 0.0036
Circuit | 042202 | [8 empty] | 30 | [21 empty] | 0.0014
Circuit | 037101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 41 | 22 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 7.7 | 0.06 | 129.34 | 0.9998 | 1.5573
Circuit | 023503 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2303 | 0 | 2027 | 23 | 0 | 0 | 0 | 208 | 45 | 0 | 0 | 39.42 | 0.67 | 59.26 | 0.9991 | 0.0131
Circuit | 050302 |  |  | 1
Circuit | 098302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 0.01 | 143.72 | 1
Circuit | 147901 |  |  |  |  | 1 | 0.991 |  |  | 1 | [6 empty] | 117 | 53 | 0 | 0 | 0 | 0 | 61 | 0 | 3 | 0 | 0 | 11.78 | 0.1 | 119.45 | 0.9997 | 0.0059
Circuit | 066301 |  |  |  |  | 1 |  | 1 |  | 0 | 0 |  |  | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.34 | 0.01 | 165.47 | 0.9999
Circuit | 011201 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 3 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.44 | 0 | 135.31 | 1 | 0.0211
Circuit | 000403 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 5.02 | 0.01 | 338.06 | 0.9999 | 0.0032
Circuit | 129002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 118 | 0 | 0 | 1 | 0 | 0 | 117 | 0 | 0 | 0 | 0 | 6.2 | 0.05 | 127.06 | 0.9999 | 0.0008
Circuit | 049702 |  |  |  |  | 1 | 1 | 1 |  | 8 | [6 empty] | 290 | 42 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 11.02 | 0.22 | 50.72 | 0.9997 | 0.006
Circuit | 032002 | [8 empty] | 1 | [21 empty] | 0.0035
Circuit | 000201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.72 | 0.01 | 166.84 | 1 | 0.0005
Circuit | 061806 | [8 empty] | 0
Circuit | 135904 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0.51 | 0.01 | 64.35 | 1 | 0.0539
Circuit | 063501 | [8 empty] | 0 | [21 empty] | 0.3455
Circuit | 066402 | [8 empty] | 0 | [21 empty] | 0.0031
Circuit | 000902 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 1 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 87.76 | 0.44 | 199.14 | 0.998 | 0.3186
Circuit | 057001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 123 | 1 | 0.0654
Circuit | 085801 |  |  |  |  | 1 |  | 1 |  | 0 | 0 |  |  | 0 | 0 | 0 | 6 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 0.01 | 231.27 | 1 | 0.0124
Circuit | 014603 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 43 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 16.34 | 0.11 | 149.36 | 0.9996
Circuit | 153601 |  |  | 0 | [5 empty] | 1 | [21 empty] | 0.0121
Circuit | 135903 | [8 empty] | 0 | [21 empty] | 0.0006
Circuit | 053402
Circuit | 049802 |  |  | 0 |  | 1 | 0.95 |  |  | 0 | 0.56 |  |  | 0 | 267.72 | 1.01 | 20 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 1 | 0 | 0 | 2.72 | 0.01 | 183.71 | 0.9999 | 0.0044
Circuit | 122901 |  |  | 1 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 13 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 1 | 0.98 | 0.01 | 106.33 | 1 | 0.0311
Circuit | 137202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 455 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.5 | 0.68 | 88.13 | 0.9986 | 0.092
Circuit | 128403 | [30 empty] | 0.002
Circuit | 109201 |  |  |  |  | 1 | 0.929 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 29 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 4.33 | 0.01 | 309.29 | 0.9999 | 2.2845
Circuit | 062901 | [8 empty] | 0 | [21 empty] | 0.006
Circuit | 036203 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 169 | 1 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 1.76 | 0.14 | 12.6 | 1 | 0.0043
Circuit | 108101 |  |  |  |  | 1 | 0.995 |  |  | 0 | [6 empty] | 187 | 0 | 0 | 0 | 0 | 0 | 2 | 185 | 0 | 0 | 0 | 158.6 | 0.43 | 369.79 | 0.9963 | 2.5482
Circuit | 135301 | [8 empty] | 1 | [21 empty] | 0.0061
Circuit | 055103 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29 | 0 | 469 | 1 | 0.0044
Circuit | 108802 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.003
Circuit | 077403
Circuit | 019601 | [8 empty] | 0
Circuit | 024702 | [8 empty] | 0
Circuit | 050803 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 4 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.9 | 0 | 205.8 | 1 | 0.0373
Circuit | 037601 |  |  |  |  | 1 | 0 | 1 |  | 6 | [6 empty] | 115 | 1 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 22.23 | 0.14 | 160.27 | 0.9995 | 0.7069
Circuit | 022902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 124 | 0 | 0 | 0 | 0 | 0 | 121 | 1 | 2 | 0 | 0 | 23.95 | 0.19 | 126.71 | 0.9994 | 0.7698
Circuit | 090801 | [8 empty] | 0 | [21 empty] | 0.0302
Circuit | 115701 | [8 empty] | 0 | [21 empty] | 0.0014
Circuit | 062001 | [30 empty] | 0.0286
Circuit | 122702 | [8 empty] | 0
Circuit | 080802 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 106.61 | 0.12 | 900.55 | 0.9975 | 0.0436
Circuit | 159501 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 0 | 1007 | 1 | 0.0325
Circuit | 032404 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 33 | 2 | 0 | 1 | 0 | 1 | 0 | 28 | 0 | 1 | 0 | 2.66 | 0.02 | 169.82 | 0.9999 | 0.955
Circuit | 043302 | [8 empty] | 0 | [21 empty] | 0.0008
Circuit | 047601
Circuit | 017004 | [30 empty] | 0.9185
Circuit | 022403 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12.02 | 0.06 | 209.27 | 0.9997 | 0.0144
Circuit | 129801 | [30 empty] | 0.5248
Circuit | 024104 | [8 empty] | 0 | [21 empty] | 1
Circuit | 042303 | [8 empty] | 0
Circuit | 133202 | [8 empty] | 0 | [6 empty] | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0043
Circuit | 111203 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.41 | 0 | 153.86 | 1 | 0.0391
Circuit | 014302 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.62 | 0.01 | 237.81 | 0.9999
Circuit | 106603
Circuit | 137801 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 319 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 127 | 0 | 223.68 | 1 | 223.68 | 0.9948 | 1.5016
Circuit | 049401 | [8 empty] | 0 | [6 empty] | 359 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0103
Circuit | 114201 | [8 empty] | 0 | [21 empty] | 0.0044
Circuit | 011302 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1.83 | 0.01 | 234.92 | 1
Circuit | 036301 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.43 | 0 | 333 | 1 | 0.9883
Circuit | 154302 |  |  |  |  | 1 | 1 | 1 |  | 112 | 0 |  |  | 4.62 | 0 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 261.49 | 1 | 0.0026
Circuit | 007101 |  |  |  |  | 1 | 0.056 | 1 |  | 0 | [6 empty] | 19 | 1 | 0 | 0 | 0 | 0 | 17 | 1 | 0 | 0 | 0 | 68.84 | 0.08 | 862.26 | 0.9984 | 0.021
Circuit | 003701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 1.24 | 0.01 | 107.76 | 1 | 0.0106
Circuit | 001303 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1.44 | 0.01 | 188.44 | 1 | 0.0076
Circuit | 029406 | [8 empty] | 0 | [21 empty] | 0.0111
Circuit | 059402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 76 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 5.56 | 0.04 | 147.89 | 0.9999 | 0.004
Circuit | 029405 |  |  |  |  | 1 | 1 | [9 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.04 | 0 | 30.28 | 1
Circuit | 034402 |  |  |  |  | 1 | 1 | 1 |  | 34 | [6 empty] | 1612 | 1 | 361 | 0 | 0 | 0 | 172 | 213 | 0 | 15 | 850 | 40.41 | 0.52 | 77.92 | 0.9991 | 1.8349
Circuit | 148601 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0.16 | 0 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0.29 | 0 | 117.16 | 1 | 0.0041
Circuit | 055802 | [8 empty] | 0
Circuit | 161201 | [30 empty] | 0.0034
Circuit | 086003 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 170 | 7 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.72 | 0 | 145.82 | 1 | 0.146
Circuit | 110802 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 42 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 1 | 0 | 27.57 | 0.07 | 399.06 | 0.9994 | 0.0033
Circuit | 042001 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 0 | [15 empty] | 0.0066
Circuit | 161302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 109.79 | 1
Circuit | 114601 | [8 empty] | 0
Circuit | 029401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.39 | 0.01 | 459.25 | 0.9999
Circuit | 135304
Circuit | 027402 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.88 | 0.01 | 243.39 | 1 | 0.2343
Circuit | 062302 | [8 empty] | 0 | [21 empty] | 0.0039
Circuit | 049102 | [8 empty] | 0 | 1.6 |  |  | 0.54 | 2.99 | 1.09 | [15 empty] | 0.1572
Circuit | 051501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.33 | 0 | 241.5 | 1 | 0.0061
Circuit | 061702 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 3 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.44 | 0 | 161.11 | 1 | 0.0018
Circuit | 142703 |  |  | 0.5 |  | 1 | 0.528 |  |  | 0 | [6 empty] | 36 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 7.15 | 0.01 | 575.29 | 0.9998 | 0.0204
Circuit | 135202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.37 | 0 | 211.67 | 1 | 0.0017
Circuit | 151501 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 30 | 1 | 28 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5.46 | 0.04 | 150.86 | 0.9999 | 0.0012
Circuit | 008002 |  |  |  |  | 1 | 0.5 |  |  | 0 | 0 |  |  | 6.5 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.37 | 0.01 | 265.11 | 1 | 0.0052
Circuit | 045101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 1 | 0 | 0 | 5.82 | 0.04 | 155.56 | 0.9999 | 1.5421
Circuit | 066501 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0076
Circuit | 154501 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 153 | 0 | 0 | 0 | 0 | 152 | 0 | 1 | 0 | 0 | 0 | 44.07 | 0.14 | 317.4 | 0.999 | 0.0073
Circuit | 162601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 677 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 155.01 | 1 | 154.78 | 0.9964 | 0.145
Circuit | 025102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 56 | 0 | 0 | 1 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 3 | 0.03 | 89.8 | 0.9999
Circuit | 140201 |  |  |  | 1 | 1 | 0.944 |  |  | 0 | [6 empty] | 36 | 3 | 0 | 0 | 0 | 0 | 20 | 0 | 1 | 12 | 0 | 4.74 | 0.02 | 219.11 | 0.9999 | 0.1118
Circuit | 105301 |  |  |  |  | 1 | 1 |  |  | 0 | 1.17 |  |  | 1.5 | 0.78 | 0.78 | 887 | 0 | 0 | 0 | 0 | 0 | 885 | 0 | 2 | 0 | 0 | 36.51 | 0.37 | 98.12 | 0.9992 | 0.4375
Circuit | 067404 | [8 empty] | 0
Circuit | 157004 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 392 | 0 | 0 | 0 | 0 | 11 | 0 | 381 | 0 | 0 | 0 | 16.02 | 0.44 | 36.82 | 0.9996 | 0.0355
Circuit | 134801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 100 | 1
Circuit | 111801
Circuit | 058602 | [30 empty] | 0.0116
Circuit | 150802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 35 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 2.69 | 0.06 | 43.16 | 0.9999 | 0.0036
Circuit | 103501 | [30 empty] | 0.0039
Circuit | 083504 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0 | 91 | 1 | 0.0014
Circuit | 084102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 271 | 1 | 0.0037
Circuit | 122501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 480 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.23 | 0.35 | 83 | 0.9993 | 0.3375
Circuit | 073603
Circuit | 003702 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 93 | 7 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 68 | 16.15 | 0.1 | 168.94 | 0.9996 | 0.0062
Circuit | 045102 | [8 empty] | 0 | [21 empty] | 0.9844
Circuit | 037102 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6 | 0.49 | 0.01 | 38.84 | 1 | 0.3363
Circuit | 055102 | [30 empty] | 0.0022
Circuit | 061402 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 19 | 1 | 1 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 2.4 | 0.04 | 67.15 | 0.9999
Circuit | 005601 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1.01 | 0 | 701.54 | 1
Circuit | 092102 |  |  |  | 1 | 1 | 1 | 1 |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 0.38 | 0 | 118.14 | 1 | 0.166
Circuit | 001902 | [8 empty] | 0 | [21 empty] | 0.0009
Circuit | 054202 |  |  |  |  | 1 | 0.002 |  |  | 0 | 0.88 |  |  | 0 | 1 | 2.1 | 562 | 562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.71 | 1.01 | 1233.87 | 0.9712 | 0.0036
Circuit | 018301 |  |  |  |  | 1 | 0.622 |  |  | 204 | [6 empty] | 217 | 81 | 0 | 0 | 0 | 0 | 133 | 1 | 0 | 1 | 1 | 42.79 | 0.17 | 254.79 | 0.999 | 0.9954
Circuit | 036904
Circuit | 025804 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 0 | 362 | 1 | 0.971
Circuit | 017002 | [8 empty] | 0 | [21 empty] | 0.0038
Circuit | 141802 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0.54 | 0 | 297 | 1 | 1.3837
Circuit | 077101 |  |  |  |  | 1 | 0 |  |  | 26 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.64 | 0 | 1040 | 1 | 0.0016
Circuit | 034002 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 9 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 0.01 | 129.03 | 1 | 0.0029
Circuit | 063903 | [8 empty] | 0 | [21 empty] | 0.0021
Circuit | 006401 | [8 empty] | 0
Circuit | 048002 | [8 empty] | 0 | [21 empty] | 0.0124
Circuit | 066601 |  |  |  |  | 1 | 1 |  |  | 92 | [6 empty] | 32 | 4 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 4.77 | 0.04 | 122.84 | 0.9999 | 0.1735
Circuit | 051601 |  |  |  |  | 1 | 1 |  |  | 17 | [6 empty] | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 13 | 0 | 5.63 | 0.07 | 83.14 | 0.9999
Circuit | 043701 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 3 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0.01 | 209 | 1 | 0.2111
Circuit | 013802 |  |  |  | 1 | 1 | 1 |  |  | 5 | [6 empty] | 16 | 1 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 3.77 | 0.02 | 173.4 | 0.9999 | 0.4457
Circuit | 066101 |  |  |  | 1 | 1 | 1 |  |  | 0 | 8.22 |  |  | 22.01 | 0.37 | 0.42 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 19 | 1 | 0.2108
Circuit | 600101 | [8 empty] | 0
Circuit | 003001 | [30 empty] | 0.0048
Circuit | 004201
Circuit | 160102 | [8 empty] | 0 | [21 empty] | 0.0021
Circuit | 017604 | [30 empty] | 0.0031
Circuit | 023507 | [30 empty] | 0.0019
Circuit | 040501 |  |  |  |  | 1 | 0.25 |  |  | 0 | [6 empty] | 8 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 6.14 | 0.01 | 477.84 | 0.9999 | 0.0032
Circuit | 025603 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 0 | 523.2 | 1 | 0.0893
Circuit | 128803
Circuit | 033804 |  |  |  |  | 1 |  | 1 |  | 0 | 3.45 |  |  | 4.03 | 0.86 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.36 | 0 | 166 | 1 | 0.0044
Circuit | 023402 |  |  | 1 |  | 1 | 1 | 1 |  | 47 | [6 empty] | 32 | 0 | 0 | 0 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 2.42 | 0.02 | 134.37 | 0.9999 | 0.1226
Circuit | 034203 | [8 empty] | 0
Circuit | 150702 |  |  | 1 |  | 1 | 1 |  |  | 2 | [6 empty] | 107 | 81 | 0 | 25 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6.22 | 0.06 | 104.04 | 0.9999 | 0.0955
Circuit | 036401 | [30 empty] | 0.004
Circuit | 063802 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 570 | 0 | 0 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 349.26 | 1.06 | 328.43 | 0.9919 | 2.3918
Circuit | 014901 |  |  |  |  | 1 | 1 |  |  | 117 | [6 empty] | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 13 | 2.31 | 0.02 | 95.6 | 0.9999 | 0.006
Circuit | 051901 |  |  |  |  | 1 | 0.227 |  |  | 1 | [6 empty] | 66 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 10 | 0 | 15.2 | 0.03 | 452.94 | 0.9996 | 0.3777
Circuit | 018902 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 15 | 0 | 13 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2.09 | 0.02 | 123.34 | 1 | 0.3303
Circuit | 044201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.05 | 0 | 82.97 | 1 | 0.657
Circuit | 078402 | [9 empty] | 0 |  |  | 0 | 0 | 1 | [15 empty] | 0.0625
Circuit | 114302 |  |  |  |  | 1 | 1 |  |  | 0 | 10.65 |  |  | 39.11 | 0.27 | 0.58 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 54 | 1 | 0.0037
Circuit | 055801 | [8 empty] | 0 | [21 empty] | 0.0161
Circuit | 145101 | [8 empty] | 0 | [21 empty] | 0.6866
Circuit | 045701 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 1 | [15 empty] | 0.0039
Circuit | 031002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 10.06 | 0.05 | 204.56 | 0.9998 | 0.0753
Circuit | 040902 | [8 empty] | 1 | [21 empty] | 0.3373
Circuit | 147902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 28 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 6.63 | 0.05 | 137.96 | 0.9998 | 0.0017
Circuit | 138303 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.42 | 0 | 112.98 | 1 | 1.1922
Circuit | 155401 |  |  |  |  | 1 | 1 |  |  | 14 | [6 empty] | 1452 | 1429 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 1 | 58.06 | 1.02 | 56.74 | 0.9987 | 0.031
Circuit | 029203 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2.24 | 0.02 | 126.96 | 0.9999 | 0.0026
Circuit | 048202 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.56 | 0 | 617 | 1 | 0.0036
Circuit | 048401 | [30 empty] | 0.2788
Circuit | 103502 | [8 empty] | 0 | [21 empty] | 0.0027
Circuit | 157003 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 800 | 0 | 0 | 0 | 0 | 796 | 4 | 0 | 0 | 0 | 0 | 224.04 | 1.05 | 214.24 | 0.9948 | 0.2745
Circuit | 124402 | [8 empty] | 1 | 0 |  |  | 7.05 | 0 | 0 | [15 empty] | 0.003
Circuit | 163502 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.29 | 0 | 238.23 | 1
Circuit | 022402 | [8 empty] | 0 | [21 empty] | 0.0216
Circuit | 051504 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.54 | 0.01 | 55.15 | 1 | 0.001
Circuit | 022405 | [8 empty] | 0 | [21 empty] | 0.0789
Circuit | 133504 |  |  |  |  | 1 | 0.6 | 1 |  | 0 | [6 empty] | 91 | 1 | 88 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 10.08 | 0.13 | 78.74 | 0.9998
Circuit | 070201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 136 | 1
Circuit | 073302 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 285 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 11.42 | 0.2 | 58.04 | 0.9997 | 0.0083
Circuit | 157601 |  |  |  |  | 1 | 1 |  |  | 0 | 3.45 |  |  | 13.07 | 0.26 | 0.26 | 44 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 1 | 0 | 7.02 | 0.1 | 73.03 | 0.9998 | 0.0131
Circuit | 050102 | [8 empty] | 0 | [21 empty] | 0.0048
Circuit | 077604 | [8 empty] | 0
Circuit | 065502 | [8 empty] | 0
Circuit | 126301 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 304 | 1 | 1 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 1 | 0.57 | 0 | 298.63 | 1 | 0.0424
Circuit | 000703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.18 | 0 | 145.8 | 1 | 0.0012
Circuit | 025801 | [8 empty] | 0 | [21 empty] | 0.955
Circuit | 125802 | [8 empty] | 0 | [21 empty] | 0.1992
Circuit | 134002 |  |  |  |  | 1 | 1 | 1 |  | 243 | [6 empty] | 110 | 95 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 20.46 | 0.19 | 110.13 | 0.9995 | 0.0084
Circuit | 115703 | [8 empty] | 0
Circuit | 095401
Circuit | 004101 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 92.76 | 1 | 0.3518
Circuit | 137301 | [8 empty] | 0 | [21 empty] | 0.0028
Circuit | 100204 |  |  |  |  | 1 |  | 1 |  | 0 | 2.57 |  |  | 2.57 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.78 | 0.03 | 569 | 0.9996
Circuit | 099602
Circuit | 097201 | [8 empty] | 0 | [21 empty] | 0.987
Circuit | 004502 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 1 | [15 empty] | 0.0006
Circuit | 062902 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 251 | 0 | 249 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 41.73 | 0.23 | 183.39 | 0.999 | 0.0118
Circuit | 074604 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1.02 | 0.01 | 85.96 | 1 | 0.0079
Circuit | 028302 |  |  |  |  | 1 | 1 | 1 |  | 0 | 9.55 |  |  | 3.19 | 2.99 | 1.19 | 43 | 22 | 19 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2.79 | 0.02 | 136.72 | 0.9999 | 0.0886
Circuit | 033402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.1 | 0 | 83.28 | 1 | 0.0013
Circuit | 103301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.01 | 0.04 | 175.27 | 0.9998 | 0.3106
Circuit | 081502
Circuit | 061703 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 192 | 191 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 13.58 | 0.22 | 62.8 | 0.9997 | 0.3908
Circuit | 149401
Circuit | 005501 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.61 | 0.01 | 118.7 | 1
Circuit | 079802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1423 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1422 | 0 | 413.2 | 1.97 | 209.65 | 0.9904 | 0.054
Circuit | 122201 | [8 empty] | 0 | [21 empty] | 0.265
Circuit | 045302 | [8 empty] | 0
Circuit | 046901 | [8 empty] | 0 | 0 |  |  | 2.5 | 0 | 0
Circuit | 010926
Circuit | 082902
Circuit | 084001 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 276 | 13 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 34.73 | 0.15 | 236.72 | 0.9992 | 1.1489
Circuit | 110801 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 11 | 0 | 1 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 0 | 3.4 | 0.01 | 322.69 | 0.9999 | 1.8391
Circuit | 168702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.22 | 0 | 90.41 | 1 | 0.0024
Circuit | 026501 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0.36 | 0 | 184.5 | 1 | 0.0048
Circuit | 157701 | [8 empty] | 20 | [21 empty] | 0.0025
Circuit | 058201 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 151 | 1 | 0 | 0 | 0 | 0 | 0 | 149 | 1 | 0 | 0 | 20.37 | 0.12 | 175.23 | 0.9995 | 0.077
Circuit | 067502
Circuit | 009101 |  |  |  |  | 1 | 0.667 | 1 |  | 46 | [6 empty] | 139 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 47 | 22.1 | 0.08 | 264.57 | 0.9995 | 0.8438
Circuit | 090402 |  |  | 1 |  | 1 | 1 |  |  | 0 | 0 |  |  | 6.95 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 98 | 21.46 | 0.11 | 202.49 | 0.9995 | 0.0133
Circuit | 094602 | [8 empty] | 0 | [21 empty] | 0.0828
Circuit | 013402 | [8 empty] | 0 | [21 empty] | 0.001
Circuit | 012802 |  |  |  |  | 1 | 0.982 | 1 |  | 0 | [6 empty] | 92 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 1 | 0 | 0 | 24.81 | 0.14 | 179.9 | 0.9994 | 0.0795
Circuit | 057301 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 59 | 3 | 1 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 9.1 | 0.05 | 165.72 | 0.9998 | 0.3836
Circuit | 099603
Circuit | 067402 | [8 empty] | 0 | 0 |  |  | 9.44 | 0 | 0
Circuit | 036906
Circuit | 023504 | [8 empty] | 0
Circuit | 021202 |  |  | 1 |  | 1 | 0.999 | 1 |  | 4 | [6 empty] | 1033 | 0 | 987 | 44 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 62.22 | 0.63 | 98.65 | 0.9986 | 0.368
Circuit | 011301 |  |  |  | 1 | 1 | 1 | 1 |  | 149 | [6 empty] | 95 | 0 | 0 | 0 | 0 | 13 | 0 | 44 | 38 | 0 | 0 | 8.93 | 0.07 | 122.13 | 0.9998 | 0.0085
Circuit | 113402
Circuit | 093801 | [8 empty] | 0 | [6 empty] | 66 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0025
Circuit | 034603 | [30 empty] | 0.0044
Circuit | 037402 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 4 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 129.13 | 1 | 0.0313
Circuit | 026902 |  |  |  |  | 1 | 1 | 1 |  | 0 | 0 |  |  | 5 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1.25 | 0 | 499.55 | 1 | 0.4718
Circuit | 163602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0 | 413.53 | 1
Circuit | 144301 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 31 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 2.35 | 0.03 | 79.82 | 0.9999 | 0.0048
Circuit | 007303 | [8 empty] | 0 | [21 empty] | 0.0642
Circuit | 003102 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 14 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 2.71 | 0.01 | 252.09 | 0.9999 | 0.0661
Circuit | 043602 |  |  |  | 1 | 1 | 1 | 1 |  | 4 | [6 empty] | 47 | 1 | 0 | 0 | 0 | 0 | 16 | 28 | 1 | 1 | 0 | 6.28 | 0.03 | 205.12 | 0.9999 | 0.9263
Circuit | 034701 |  |  |  |  | 1 | 0.999 | 1 |  | 0 | [6 empty] | 723 | 0 | 2 | 0 | 0 | 0 | 710 | 11 | 0 | 0 | 0 | 194.03 | 1.4 | 138.21 | 0.9955 | 3.367
Circuit | 060402 | [8 empty] | 0 | [21 empty] | 0.0017
Circuit | 004701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.15 | 0 | 108 | 1 | 0.0708
Circuit | 056302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 3.42 | 0.03 | 120.74 | 0.9999 | 0.0142
Circuit | 082501
Circuit | 002704 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0.71 | 0.02 | 37.34 | 1 | 0.0139
Circuit | 021102 | [8 empty] | 0 | [21 empty] | 0.0075
Circuit | 036102 | [8 empty] | 0 | [21 empty] | 0.0048
Circuit | 076509
Circuit | 036201 | [9 empty] | 0 |  |  | 0.23 | 0 | 1 | [15 empty] | 0.0027
Circuit | 107201 |  |  | 1 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 389 | 5 | 0 | 0 | 0 | 0 | 53 | 330 | 0 | 1 | 0 | 58.98 | 0.51 | 116.75 | 0.9986 | 0.5935
Circuit | 075402
Circuit | 049205 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38 | 0.01 | 221.51 | 0.9999
Circuit | 121004 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 386.91 | 1
Circuit | 097202 | [8 empty] | 0 | [21 empty] | 0.9808
Circuit | 040602 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 189 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 187 | 0 | 7.65 | 0.43 | 17.65 | 0.9998 | 0.4037
Circuit | 090101 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 0
Circuit | 022401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.8 | 0.01 | 229.1 | 1 | 0.0069
Circuit | 001904 | [8 empty] | 0 | [21 empty] | 0.0055
Circuit | 009005 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0 | 412 | 1 | 0.0068
Circuit | 130903 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0.39 | 0 | 181 | 1 | 0.0021
Circuit | 062401 | [8 empty] | 0
Circuit | 002901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 1.61 | 0.03 | 47.23 | 1 | 0.4071
Circuit | 136803 | [9 empty] | 0 |  |  | 0 | 0 | 1
Circuit | 029303
Circuit | 000602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 283 | 1
Circuit | 093403 | [8 empty] | 0 | [21 empty] | 0.0068
Circuit | 140402 |  |  |  |  | 1 | 1 |  |  | 0 | 0.94 |  |  | 0.94 | 1 | 1 | 35 | 33 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2.74 | 0.02 | 130.55 | 0.9999 | 1.6438
Circuit | 152702 | [8 empty] | 0
Circuit | 099801 | [8 empty] | 0 | [21 empty] | 0.0007
Circuit | 021303 | [8 empty] | 0 | [21 empty] | 0.0097
Circuit | 119602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 0 | 211 | 1 | 0.0025
Circuit | 049403 | [8 empty] | 0
Circuit | 028003 | [8 empty] | 0 | 0 |  |  | 1.98 | 0 | 0
Circuit | 021302 | [8 empty] | 31 | [21 empty] | 0.002
Circuit | 160101 | [8 empty] | 0 | [21 empty] | 0.658
Circuit | 061701
Circuit | 058601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 28 | 0 | 0 | 0 | 0 | 27 | 1 | 0 | 0 | 0 | 0 | 2.6 | 0.04 | 72.92 | 0.9999 | 0.014
Circuit | 037701 |  |  |  |  | 1 | 0.6 |  |  | 25 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 2.79 | 0.01 | 456.3 | 0.9999 | 0.661
Circuit | 114701 | [8 empty] | 0
Circuit | 087704 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 69 | 19 | 0 | 1 | 0 | 0 | 33 | 0 | 16 | 0 | 0 | 5.26 | 0.04 | 132.46 | 0.9999 | 0.1413
Circuit | 009902 |  |  | 1 |  | 1 | 0.995 |  |  | 0 | 0.17 |  |  | 2.09 | 0.08 | 0.08 | 747 | 641 | 0 | 0 | 0 | 89 | 15 | 0 | 0 | 1 | 1 | 66.49 | 0.35 | 191.03 | 0.9985 | 0.7102
Circuit | 109501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 82 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 10.95 | 0.08 | 132.48 | 0.9997 | 0.2429
Circuit | 091702
Circuit | 039505 | [8 empty] | 0
Circuit | 106901 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 187 | 145 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.21 | 0.29 | 224.51 | 0.9985 | 0.0335
Circuit | 035001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.94 | 0.01 | 181.37 | 1 | 0.0118
Circuit | 017006 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.95 | 0.02 | 176.57 | 0.9999 | 0.0004
Circuit | 078003 | [8 empty] | 0 | [21 empty] | 0.0243
Circuit | 043902 |  |  |  |  | 1 | 1 |  |  | 16 | 0 |  |  | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 0.01 | 96 | 1 | 0.0059
Circuit | 083802 | [8 empty] | 0
Circuit | 020702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.01 | 0 | 12.21 | 1 | 0.0021
Circuit | 066504 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 38 | 0 | 7.86 | 0.08 | 97.31 | 0.9998 | 0.4012
Circuit | 010601 | [8 empty] | 0
Circuit | 041701 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0.28 | 0 | 57 | 1 | 0.0897
Circuit | 002903 | [8 empty] | 0
Circuit | 154102 | [8 empty] | 0 | 0 |  |  | 2.54 | 0 | 0.76
Circuit | 107702 |  |  |  | 1 |  |  |  |  | 0 | [21 empty] | 0.9925
Circuit | 030001 | [8 empty] | 0
Circuit | 010705
Circuit | 042401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 489 | 489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9 | 0.65 | 142.26 | 0.9979 | 0.6169
Circuit | 156601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.07 | 0 | 474 | 1 | 0.2275
Circuit | 034201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 4.32 | 0.04 | 105.16 | 0.9999
Circuit | 061704 | [8 empty] | 0 | 2.4 |  |  | 0.14 | 16.99 | 1.91
Circuit | 051503 | [30 empty] | 0.0034
Circuit | 087703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 0.03 | 67.84 | 1
Circuit | 144202 | [8 empty] | 0 | [21 empty] | 0.001
Circuit | 058001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 106.69 | 1 | 0.0013
Circuit | 017502 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 11.57 | 0.01 | 909.32 | 0.9997 | 0.0017
Circuit | 025803 | [8 empty] | 0 | 0 |  |  | 1.74 | 0 | 0.75 | [15 empty] | 0.962
Circuit | 027803 | [8 empty] | 0 | [21 empty] | 0.0076
Circuit | 014101 | [8 empty] | 0
Circuit | 073604 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 31 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.39 | 0.1 | 133.04 | 0.9997 | 0.4026
Circuit | 076511 | [8 empty] | 0 | [21 empty] | 0.0025
Circuit | 114301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 76 | 13 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 1 | 0 | 20.81 | 0.08 | 263.1 | 0.9995 | 0.283
Circuit | 042502 |  |  |  |  | 1 | 1 | 1 |  | 856 | [6 empty] | 2700 | 1 | 0 | 2143 | 0 | 448 | 2 | 0 | 0 | 106 | 0 | 42.97 | 0.26 | 165.07 | 0.999 | 0.4551
Circuit | 047502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 146.32 | 1 | 0.001
Circuit | 070104 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 19 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0.62 | 0.02 | 37.32 | 1 | 0.0488
Circuit | 150801 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 41 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 10.16 | 0.09 | 111 | 0.9998 | 0.0446
Circuit | 137101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 117 | 0 | 0 | 0 | 0 | 0 | 40 | 77 | 0 | 0 | 0 | 13.59 | 0.11 | 126.69 | 0.9997 | 0.791
Circuit | 008001 |  |  |  |  | 1 | 0.833 | 1 |  | 0 | [6 empty] | 50 | 2 | 2 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 3.71 | 0.03 | 107.72 | 0.9999 | 0.0021
Circuit | 051502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0.13 | 0 | 36.46 | 1 | 0.381
Circuit | 010007 | [8 empty] | 0 | 1.05 |  |  | 0 | 1 | 1
Circuit | 023508
Circuit | 019201 |  |  |  |  | 1 | 1 | 1 |  | 5 | [6 empty] | 102 | 1 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 1 | 0 | 25.53 | 0.31 | 81.58 | 0.9994 | 0.5092
Circuit | 021901 | [8 empty] | 0 | [21 empty] | 0.0031
Circuit | 042302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 309 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 57.83 | 0.43 | 134.18 | 0.9987 | 0.304
Circuit | 023801 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 71 | 3 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5.34 | 0.05 | 108.3 | 0.9999 | 0.2847
Circuit | 113602 | [8 empty] | 0 | [21 empty] | 0.006
Circuit | 092002 | [8 empty] | 0 | [21 empty] | 0.0032
Circuit | 127002 |  |  |  | 0 | 1 | 1 | 1 |  | 0 | [6 empty] | 187 | 16 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 63.34 | 0.28 | 223.9 | 0.9985 | 0.6672
Circuit | 010603 | [8 empty] | 0 | [21 empty] | 0.5778
Circuit | 006707 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 53 | 0 | 0 | 3 | 0 | 0 | 46 | 0 | 0 | 4 | 0 | 1.8 | 0.03 | 58.36 | 1 | 0.2816
Circuit | 060202 |  |  |  |  | 1 | 0.998 | 1 |  | 4 | [6 empty] | 656 | 37 | 0 | 0 | 0 | 0 | 618 | 1 | 0 | 0 | 0 | 308.93 | 1.19 | 258.54 | 0.9928 | 0.8998
Circuit | 102602 | [30 empty] | 0.9972
Circuit | 157602 | [8 empty] | 31 | [21 empty] | 0.0134
Circuit | 006201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 529 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 40.89 | 0.41 | 98.87 | 0.9991 | 0.183
Circuit | 073102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 1.66 | 0.03 | 50.86 | 1
Circuit | 060602 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 274 | 3 | 0 | 194 | 0 | 0 | 76 | 0 | 0 | 1 | 0 | 25.27 | 0.1 | 264.41 | 0.9994 | 0.0167
Circuit | 000301 | [8 empty] | 0 | [21 empty] | 0.0044
Circuit | 115002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 69 | 1 | 0.1977
Circuit | 136002 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 80 | 2 | 76 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 30.39 | 0.06 | 480.99 | 0.9993 | 1.1272
Circuit | 014103 | [8 empty] | 0 | [21 empty] | 0.0023
Circuit | 003801 | [8 empty] | 0 | [21 empty] | 0.0037
Circuit | 078602 | [8 empty] | 0 | [21 empty] | 0.0044
Circuit | 078302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1.52 | 0.01 | 166 | 1 | 0.0018
Circuit | 025403 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 26 | 1 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 5.49 | 0.04 | 129.81 | 0.9999 | 0.0016
Circuit | 022501 | [30 empty] | 0.006
Circuit | 039401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.08 | 0 | 84 | 1 | 0.0057
Circuit | 135602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.17 | 0 | 89.37 | 1 | 0.001
Circuit | 033903 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 2104 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 2087 | 0 | 281.71 | 1.98 | 142 | 0.9935 | 0.0399
Circuit | 074401 | [8 empty] | 0
Circuit | 022201 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 332 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 1 | 0 | 3 | 59.53 | 0.32 | 183.44 | 0.9986 | 0.2884
Circuit | 160401 |  |  |  |  | 1 | 0.941 |  |  | 0 | 0 |  |  | 0 | 0 | 0.76 | 17 | 1 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 6.11 | 0.05 | 119.02 | 0.9999 | 0.1178
Circuit | 076001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.01 | 0 | 16 | 1 | 0.0024
Circuit | 054102 | [8 empty] | 0
Circuit | 093502 | [8 empty] | 0 | [21 empty] | 0.0006
Circuit | 148501 | [30 empty] | 0.0025
Circuit | 078202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 132 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 30.67 | 0.22 | 140.13 | 0.9993 | 1.4494
Circuit | 157403
Circuit | 043301 | [30 empty] | 0.033
Circuit | 070305 | [8 empty] | 0 | 0 |  |  | 6.65 | 0 | 0 | [15 empty] | 0.0107
Circuit | 112801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92 | 0 | 236.26 | 1 | 0.002
Circuit | 024102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 20 | 1 | 1.0038
Circuit | 156602
Circuit | 085603
Circuit | 137302 |  |  |  |  | 1 | 1 |  |  | 104 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.11 | 0 | 279 | 1 | 0.0011
Circuit | 141801
Circuit | 081603 | [8 empty] | 0 | [21 empty] | 0.0045
Circuit | 027902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 127 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 120 | 0 | 6.51 | 0.04 | 153 | 0.9998 | 0.0027
Circuit | 029601 |  |  |  |  | 1 | 1 |  |  | 105 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.16 | 0 | 129 | 1 | 0.0101
Circuit | 076402 | [8 empty] | 0 | [21 empty] | 0.0026
Circuit | 074801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1.84 | 0.02 | 87.18 | 1 | 0.2163
Circuit | 163802 |  |  |  |  | 1 | 1 |  |  | 23 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59 | 0 | 143 | 1 | 0.377
Circuit | 032503 | [8 empty] | 0 | [21 empty] | 0.0289
Circuit | 155302 | [8 empty] | 0 | [21 empty] | 0.0079
Circuit | 064701
Circuit | 036002 | [8 empty] | 0 | [21 empty] | 0.0016
Circuit | 039302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 104 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 31.59 | 0.12 | 263.08 | 0.9993 | 0.0035
Circuit | 029101 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 107 | 1 | 0.0033
Circuit | 133902 |  |  |  |  | 1 | 1 |  |  | 3 | [6 empty] | 43 | 39 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 1 | 4.71 | 0.03 | 148.62 | 0.9999 | 0.0007
Circuit | 054403 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 2 | 0 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 0 | 0.42 | 0 | 88.23 | 1 | 0.0016
Circuit | 037401 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.42 | 0 | 319 | 1 | 0.1045
Circuit | 090403 | [9 empty] | 0 |  |  | 11.82 | 0 | 0 | [15 empty] | 0.0045
Circuit | 014401 |  |  |  |  | 1 | 0.926 |  |  | 0 | [6 empty] | 27 | 13 | 1 | 0 | 0 | 0 | 8 | 1 | 2 | 1 | 1 | 5.73 | 0.03 | 206.41 | 0.9999 | 0.0206
Circuit | 011002 | [8 empty] | 0 | [21 empty] | 0.0006
Circuit | 025903 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.34 | 0 | 160.32 | 1 | 0.0021
Circuit | 106302 | [8 empty] | 0
Circuit | 052003 | [8 empty] | 0 | 6.3 |  |  | 10.74 | 0.59 | 0.61
Circuit | 063202 |  |  |  |  | 1 | 0.992 |  |  | 0 | [6 empty] | 128 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 1 | 0 | 17.2 | 0.13 | 127.53 | 0.9996
Circuit | 085902 | [8 empty] | 0
Circuit | 085602 | [8 empty] | 0 | [21 empty] | 0.0015
Circuit | 090602 | [8 empty] | 0 | [6 empty] | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.031
Circuit | 090806
Circuit | 069102
Circuit | 033802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.44 | 0.01 | 83.68 | 1 | 0.0219
Circuit | 050503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.01 | 0.01 | 186.64 | 1 | 1.9568
Circuit | 006104
Circuit | 078201 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 51.45 | 1 | 0.0095
Circuit | 010202 | [8 empty] | 0 | [21 empty] | 0.0011
Circuit | 027801 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0 | 248.78 | 1 | 0.0149
Circuit | 154301 |  |  |  |  | 1 | 1 | 1 |  | 26 | [6 empty] | 146 | 0 | 0 | 0 | 0 | 0 | 144 | 1 | 0 | 1 | 0 | 39.29 | 0.15 | 264.56 | 0.9991 | 0.1516
Circuit | 022303 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 6 | 0 | 2 | 0 | 0 | 0 | 2 | 1 | 0 | 1 | 0 | 6.02 | 0.03 | 205.54 | 0.9999 | 0.0488
Circuit | 034204 | [30 empty] | 0.002
Circuit | 149602 |  |  | 1 |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72 | 0.01 | 432.5 | 0.9999 | 0.0031
Circuit | 029102 | [8 empty] | 0
Circuit | 057102 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 20.35 | 0.02 | 944.98 | 0.9995 | 0.9651
Circuit | 093601 | [8 empty] | 0
Circuit | 024802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.24 | 0 | 169.39 | 1 | 0.0093
Circuit | 058901 |  |  |  |  | 1 | 1 |  |  | 31 | [6 empty] | 628 | 0 | 0 | 598 | 0 | 0 | 1 | 29 | 0 | 0 | 0 | 17.2 | 0.08 | 229.3 | 0.9996 | 0.0175
Circuit | 147301
Circuit | 060802 | [8 empty] | 0 | [21 empty] | 0.0043
Circuit | 000704 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 0.57 | 0.01 | 113.78 | 1 | 0.006
Circuit | 017003 | [8 empty] | 0 | [21 empty] | 0.0005
Circuit | 122902 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 1 | [15 empty] | 0.0661
Circuit | 125605 | [8 empty] | 0 | [21 empty] | 0.0008
Circuit | 059902 |  |  |  |  | 1 | 0.667 | 1 |  | 0 | [6 empty] | 4 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.84 | 0 | 454.06 | 1 | 0.0041
Circuit | 018101 | [8 empty] | 0
Circuit | 000802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0 | 159.29 | 1 | 0.9965
Circuit | 150002 | [8 empty] | 0 | 0 |  |  | 3.9 | 0 | 0 | [15 empty] | 0.0047
Circuit | 076507
Circuit | 075701 | [8 empty] | 0
Circuit | 041503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.05 | 0 | 53 | 1 | 0.0028
Circuit | 152309 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1702 | 0 | 0 | 0 | 0 | 0 | 1702 | 0 | 0 | 0 | 0 | 109.14 | 1 | 108.75 | 0.9975 | 0.5313
Circuit | 010911 | [30 empty] | 0.0039
Circuit | 057302 |  |  |  |  | 1 | 0.75 |  |  | 0 | [6 empty] | 4 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 2.24 | 0.01 | 397.31 | 0.9999 | 0.0197
Circuit | 037901 |  |  |  |  | 1 | 1 |  |  | 5 | [6 empty] | 16 | 0 | 13 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1.32 | 0.01 | 103.27 | 1 | 0.0208
Circuit | 004702 |  |  |  |  | 1 | 1 | 1 |  | 35 | 2.45 |  |  | 20.1 | 0.12 | 0.12 | 276 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 36 | 0 | 125.06 | 1.27 | 98.33 | 0.9971 | 0.8986
Circuit | 016204 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0259
Circuit | 010105 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0.36 | 0 | 287.75 | 1 | 0.0112
Circuit | 032103 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 2.78 | 0.01 | 300.12 | 0.9999 | 0.9865
Circuit | 038302
Circuit | 075101 | [8 empty] | 0 | [21 empty] | 0.0032
Circuit | 029902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1016 | 2 | 0 | 1001 | 0 | 0 | 1 | 0 | 12 | 0 | 0 | 0.48 | 0.01 | 68.19 | 1 | 0.0005
Circuit | 117904 | [8 empty] | 0
Circuit | 085608
Circuit | 027503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37 | 0 | 391.92 | 1
Circuit | 103302 | [8 empty] | 0 | [21 empty] | 0.0041
Circuit | 050303 | [30 empty] | 1.4985
Circuit | 041501
Circuit | 070003 |  |  |  |  | 1 | 1 |  |  | 0 | 0.2 |  |  | 5.55 | 0.04 | 0.25 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 2.07 | 0.02 | 118.02 | 1 | 0.3971
Circuit | 069801 |  |  |  |  | 1 | 0.333 |  |  | 0 | [6 empty] | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.9 | 0 | 406.33 | 1 | 0.0022
Circuit | 098501 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 197 | 1 | 195 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 41.54 | 0.4 | 104.17 | 0.999 | 0.1012
Circuit | 016203 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 21.6 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0 | 119.43 | 1 | 0.0794
Circuit | 076604 | [30 empty] | 0.0088
Circuit | 128402 | [8 empty] | 1 | [21 empty] | 1.6431
Circuit | 104302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 5.09 | 0.03 | 177.2 | 0.9999 | 0.2029
Circuit | 027401 |  |  |  |  | 1 | 1 | 1 |  | 180 | 0 |  |  | 0 | 7.49 | 0.87 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.2 | 0.01 | 142.12 | 1 | 0.3125
Circuit | 031702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.02 | 0 | 36.98 | 1 | 0.0086
Circuit | 112004 | [8 empty] | 0 | 1.77 |  |  | 1.77 | 1 | 1 | [15 empty] | 0.0011
Circuit | 030201 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 51 | 4 | 0 | 0 | 0 | 0 | 46 | 1 | 0 | 0 | 0 | 3.56 | 0.03 | 128.28 | 0.9999 | 0.037
Circuit | 064704 |  |  |  |  | 1 | 1 | 1 |  | 0 | 5.7 |  |  | 12.02 | 0.47 | 0.52 | 57 | 1 | 0 | 29 | 0 | 0 | 0 | 12 | 0 | 14 | 1 | 3.82 | 0.02 | 250 | 0.9999 | 0.0082
Circuit | 041101 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 15.74 | 0.08 | 186.61 | 0.9996 | 0.0005
Circuit | 038101 |  |  | 0.5 |  | 1 | 1 |  |  | 0 | [6 empty] | 1149 | 84 | 0 | 0 | 0 | 1058 | 7 | 0 | 0 | 0 | 0 | 25.94 | 1.09 | 23.89 | 0.9994 | 1.0879
Circuit | 028201 |  |  |  |  | 1 | 1 |  |  | 29 | [6 empty] | 3 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.76 | 0 | 190.95 | 1 | 0.0838
Circuit | 053303 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 119 | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | 32.34 | 0.15 | 222.05 | 0.9993 | 0.0024
Circuit | 122401 |  |  |  |  | 1 | 0.75 | 1 |  | 0 | [6 empty] | 5 | 1 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2.13 | 0.01 | 353.77 | 1 | 0.3345
Circuit | 063801 |  |  |  |  | 1 | 1 | 1 |  | 153 | [6 empty] | 335 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 336.6 | 1.01 | 334.59 | 0.9922 | 0.6216
Circuit | 063102 | [8 empty] | 0 | 1.89 |  |  | 1.89 | 1 | 1 | [15 empty] | 0.7053
Circuit | 048501 |  |  |  |  | 1 | 1 |  |  | 45 | [6 empty] | 118 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 2 | 0 | 0 | 10.67 | 0.16 | 66.47 | 0.9998 | 0.7946
Circuit | 025902 |  |  |  |  | 1 | 0.941 |  |  | 175 | [6 empty] | 17 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 1 | 0 | 5.18 | 0.03 | 198.69 | 0.9999 | 0.1365
Circuit | 022301 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 25 | 9 | 0 | 0 | 0 | 0 | 1 | 7 | 0 | 8 | 0 | 4.64 | 0.04 | 129.64 | 0.9999 | 0.093
Circuit | 050402 | [30 empty] | 1
Circuit | 096201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 110.46 | 1
Circuit | 003502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 2 | 2.88 | 0.02 | 123.46 | 0.9999 | 0.0332
Circuit | 112502 | [8 empty] | 0 | [21 empty] | 0.9365
Circuit | 079703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 33 | 32 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2.29 | 0.03 | 88.77 | 0.9999 | 0.0932
Circuit | 072301 |  |  |  |  | 1 | 0.001 | 1 |  | 0 | [6 empty] | 878 | 867 | 0 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 522.46 | 1.02 | 511.14 | 0.9879 | 1.3298
Circuit | 008203 | [8 empty] | 0 | [6 empty] | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0082
Circuit | 115904
Circuit | 010906 | [30 empty] | 0.0476
Circuit | 025802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 62 | 1 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 4.44 | 0.04 | 122.97 | 0.9999 | 1.2712
Circuit | 002902 | [8 empty] | 0 | [21 empty] | 0.0096
Circuit | 033502 | [8 empty] | 0 | [21 empty] | 0.137
Circuit | 108201 | [8 empty] | 0 | [21 empty] | 0.9629
Circuit | 151601 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 856 | 392 | 0 | 0 | 41 | 0 | 423 | 0 | 0 | 0 | 0 | 189.71 | 1.76 | 107.78 | 0.9956 | 0.1382
Circuit | 153001 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 0 | 268 | 1 | 0.2067
Circuit | 034801 |  |  | 0.667 |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 1 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 1.31 | 0.01 | 97.51 | 1
Circuit | 155402 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 29.44 | 0.03 | 1127.02 | 0.9993 | 0.0058
Circuit | 135902 |  |  |  |  | 1 | 1 |  |  | 3 | [6 empty] | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0 | 174.45 | 1 | 0.0031
Circuit | 073502 | [8 empty] | 0
Circuit | 112504 | [8 empty] | 1 | [21 empty] | 0.9402
Circuit | 060203 |  |  |  | 1 | 1 | 1 |  |  | 20 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 1.98 | 0.02 | 101.37 | 1 | 0.0084
Circuit | 031901 | [8 empty] | 0 | [6 empty] | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0053
Circuit | 025702 |  |  |  |  | 1 | 1 |  |  | 5 | [6 empty] | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 4.91 | 0.06 | 79.33 | 0.9999
Circuit | 127602 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.25 | 0.01 | 219.25 | 1 | 0.0057
Circuit | 129602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.75 | 0.01 | 142.01 | 1 | 0.0079
Circuit | 112103 |  |  |  |  | 1 | 1 |  |  | 0 | 9.88 |  |  | 22.4 | 0.44 | 0.83 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82 | 0 | 414 | 1 | 0.4504
Circuit | 070901 |  |  | 1 |  | 1 | 0.956 | 1 |  | 0 | [6 empty] | 79 | 0 | 0 | 0 | 0 | 0 | 41 | 1 | 0 | 1 | 36 | 23.12 | 0.18 | 126.73 | 0.9995 | 0.1339
Circuit | 070704 | [9 empty] | 0 |  |  | 0.98 | 0 | 0
Circuit | 056601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 95 | 1 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 17.53 | 0.06 | 276.31 | 0.9996 | 0.1216
Circuit | 078801 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 789 | 0 | 0 | 0 | 0 | 0 | 789 | 0 | 0 | 0 | 0 | 162.86 | 0.83 | 195.27 | 0.9962 | 0.3858
Circuit | 002002 |  |  |  |  | 1 | 1 |  |  | 0 | 33.87 |  |  | 71.38 | 0.47 | 0.66 | 393 | 1 | 310 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 44.41 | 0.31 | 141.16 | 0.999 | 2.6813
Circuit | 125801 | [8 empty] | 0 | [21 empty] | 0.0026
Circuit | 010008 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 271.74 | 1 | 0.0028
Circuit | 138101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 0.73 | 0 | 179.3 | 1 | 0.1052
Circuit | 083502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.39 | 0.01 | 150.12 | 1 | 0.0031
Circuit | 014902 |  |  |  |  | 1 | 0.75 | 1 |  | 187 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 1 | 1 | 0.99 | 0 | 218.53 | 1 | 0.0308
Circuit | 028202 |  |  |  |  | 1 | 1 |  |  | 230 | [6 empty] | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0.71 | 0.02 | 44.27 | 1 | 0.0241
Circuit | 016502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 0.01 | 243 | 1
Circuit | 149001
Circuit | 043502 | [8 empty] | 0
Circuit | 113403
Circuit | 073601
Circuit | 090502
Circuit | 049904 | [30 empty] | 0.0043
Circuit | 104301
Circuit | 100302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0.8 | 0.01 | 67.29 | 1 | 0.1625
Circuit | 051001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 0 | 346.37 | 1 | 0.4148
Circuit | 021204 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.13 | 0 | 82.08 | 1 | 0.0024
Circuit | 011501 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 119.91 | 1.04 | 115.47 | 0.9972 | 0.6538
Circuit | 054801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 21 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.75 | 0.01 | 241.91 | 1 | 0.3001
Circuit | 044002
Circuit | 127902 | [8 empty] | 0 | [21 empty] | 0.0031
Circuit | 028001 |  |  |  |  | 1 | 0.833 | 1 |  | 0 | [6 empty] | 7 | 2 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 1.66 | 0.01 | 304.68 | 1 | 0.0031
Circuit | 065702 |  |  |  | 0 | 1 | 1 |  |  | 0 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0.09 | 0 | 18.94 | 1 | 0.0019
Circuit | 108202 | [30 empty] | 0.9907
Circuit | 053601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 191 | 6 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 15.44 | 0.09 | 168.26 | 0.9996 | 0.0567
Circuit | 085903
Circuit | 147501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.9 | 0.01 | 131 | 1
Circuit | 070301
Circuit | 047602
Circuit | 057703 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 43 | 1 | 13 | 28 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3.75 | 0.02 | 203.06 | 0.9999 | 0.936
Circuit | 038001 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 25 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 4.75 | 0.04 | 120.15 | 0.9999 | 0.0506
Circuit | 072201 | [8 empty] | 0 | [21 empty] | 0.9819
Circuit | 006502 | [8 empty] | 0 | [6 empty] | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.02
Circuit | 024103 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 11 | 0 | 0 | 3.1 | 0.01 | 278.83 | 0.9999 | 0.9866
Circuit | 088204 |  |  |  |  | 1 | 0 |  |  | 1 | 9.79 |  |  | 8.7 | 1.12 | 1.01 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 0 | 529 | 1 | 0.0063
Circuit | 063601 | [8 empty] | 0 | [21 empty] | 0.0091
Circuit | 093501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 157 | 149 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.97 | 0.13 | 453.41 | 0.9986 | 0.0117
Circuit | 041801 | [8 empty] | 0 | [21 empty] | 0.0019
Circuit | 127402 | [8 empty] | 0 | [21 empty] | 0.0169
Circuit | 128802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.5 | 0 | 292 | 1 | 0.0009
Circuit | 076601 | [8 empty] | 0 | [21 empty] | 0.0018
Circuit | 063301 | [8 empty] | 0
Circuit | 030302 |  |  |  |  | 1 | 1 | 1 |  | 122 | [6 empty] | 431 | 0 | 0 | 0 | 0 | 0 | 315 | 116 | 0 | 0 | 0 | 49.72 | 0.32 | 155.05 | 0.9988 | 0.064
Circuit | 157801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1.66 | 0.01 | 121.75 | 1 | 0.9673
Circuit | 036404 | [8 empty] | 0 | [21 empty] | 0.0014
Circuit | 006801 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 14 | 1 | 0 | 0 | 0 | 0.98 | 0.03 | 34.4 | 1 | 0.0019
Circuit | 044802 | [8 empty] | 0 | [21 empty] | 0.0031
Circuit | 000801 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0 | 218.05 | 1 | 1.3874
Circuit | 035002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.08 | 0 | 114.18 | 1 | 0.0021
Circuit | 018202 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 7.25 | 0.01 | 546.32 | 0.9998 | 0.1841
Circuit | 032502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.27 | 0 | 209.46 | 1 | 0.0026
Circuit | 085701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 20 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4.36 | 0.02 | 275.39 | 0.9999 | 0.0071
Circuit | 161202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 54.88 | 0.92 | 59.53 | 0.9987 | 0.0104
Circuit | 010702
Circuit | 077603 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0085
Circuit | 074303 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 187 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0.12 | 100.92 | 0.9997 | 0.0113
Circuit | 157802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.71 | 0 | 175 | 1 | 0.9796
Circuit | 100202
Circuit | 026001 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 108 | 17 | 88 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 18.77 | 0.17 | 107.93 | 0.9996 | 0.1095
Circuit | 102702 | [8 empty] | 0
Circuit | 070001 | [8 empty] | 0 | [21 empty] | 0.0054
Circuit | 124201 | [8 empty] | 0 | [21 empty] | 0.0024
Circuit | 154902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 0 | 1.07 | 0.01 | 88.47 | 1
Circuit | 020901 | [8 empty] | 0 | [21 empty] | 0.2875
Circuit | 014102 | [8 empty] | 0 | [21 empty] | 0.003
Circuit | 048702 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 5 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.79 | 0.01 | 72.56 | 1 | 0.1138
Circuit | 053802 |  |  |  |  | 1 | 0.091 |  |  | 0 | [6 empty] | 11 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8.13 | 0.01 | 609.25 | 0.9998 | 0.1032
Circuit | 137805 | [8 empty] | 0
Circuit | 104404 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 4.28 | 0.07 | 64.27 | 0.9999 | 0.0965
Circuit | 161901
Circuit | 041502 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 34 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 2.34 | 0.02 | 101.63 | 0.9999 | 0.002
Circuit | 070401 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 74 | 10 | 0 | 13 | 0 | 0 | 47 | 0 | 0 | 4 | 0 | 8.18 | 0.05 | 173.06 | 0.9998 | 0.0093
Circuit | 084003 | [30 empty] | 1.2059
Circuit | 161902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 24 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 21 | 0 | 0 | 3.2 | 0.04 | 74.32 | 0.9999 | 0.2473
Circuit | 070604 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 80 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 9.97 | 0.07 | 139.29 | 0.9998 | 0.0018
Circuit | 115102 | [8 empty] | 0 | [21 empty] | 0.001
Circuit | 041902 |  |  |  |  | 1 | 1 |  |  | 107 | [6 empty] | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 18.01 | 0.06 | 298.14 | 0.9996 | 0.0235
Circuit | 050403 | [8 empty] | 0 | [21 empty] | 1.9265
Circuit | 117901 | [9 empty] | 0 |  |  | 3.1 | 0 | 0.86 | [15 empty] | 0.0015
Circuit | 124501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 70 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 5.48 | 0.04 | 149.27 | 0.9999 | 0.1373
Circuit | 102102 | [8 empty] | 0 | 0 |  |  | 7.74 | 0 | 0
Circuit | 041601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.18 | 0.04 | 104.26 | 0.9999 | 0.4764
Circuit | 023102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 218 | 0 | 216 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 44.79 | 0.36 | 126.16 | 0.999 | 0.0847
Circuit | 034101 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 89.97 | 1 | 0.0114
Circuit | 090304 | [8 empty] | 0 | 0 |  |  | 12.91 | 0 | 0 | [15 empty] | 0.1455
Circuit | 058302 |  |  |  |  | 1 | 1 |  |  | 0 | 5.55 |  |  | 15.25 | 0.36 | 0.65 | 23 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 1.94 | 0.03 | 67.25 | 1 | 0.0238
Circuit | 053602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.17 | 0 | 323.69 | 1
Circuit | 133903 | [8 empty] | 0
Circuit | 082202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.16 | 0.53 | 141.73 | 0.9983
Circuit | 128801 | [30 empty] | 0.0077
Circuit | 009802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 37 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.77 | 0.04 | 133.08 | 0.9999 | 0.0048
Circuit | 104802 | [8 empty] | 0 | [21 empty] | 0.0484
Circuit | 127001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 674 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 639 | 133.82 | 0.51 | 264.46 | 0.9969 | 0.5833
Circuit | 086801 |  |  |  |  | 1 | 1 | 1 |  | 54 | 36.91 |  |  | 46.72 | 0.79 | 0.87 | 17 | 2 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 0.92 | 0.01 | 78.74 | 1 | 0.0304
Circuit | 064101 | [8 empty] | 0 | [21 empty] | 0.0017
Circuit | 073202 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.46 | 0 | 155.5 | 1
Circuit | 099103 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 59.66 | 1 | 0.8544
Circuit | 063703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 41 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 9.38 | 0.03 | 284.04 | 0.9998 | 0.2579
Circuit | 147502 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 148 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 1 | 0 | 22.11 | 0.19 | 119.21 | 0.9995 | 0.0213
Circuit | 026402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 46 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.47 | 0.08 | 126.03 | 0.9998 | 0.0033
Circuit | 072202 | [8 empty] | 0 | 2.86 |  |  | 10.23 | 0.28 | 0.58 | [15 empty] | 1.0119
Circuit | 154202 |  |  |  |  | 1 | 0.993 |  |  | 40 | [6 empty] | 663 | 0 | 0 | 525 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 114.76 | 0.52 | 219.53 | 0.9973 | 0.0076
Circuit | 085904 |  |  | 0 |  | 1 |  | 1 |  | 0 | [6 empty] | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 14.6 | 0.14 | 105 | 0.9997 | 0.0043
Circuit | 079202 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.48 | 0 | 286.91 | 1 | 0.1136
Circuit | 061807
Circuit | 034501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.61 | 0 | 389.85 | 1 | 0.0031
Circuit | 022801
Circuit | 043501 |  |  |  | 1 |  |  |  |  | 0 | [21 empty] | 0.0009
Circuit | 047301 | [30 empty] | 0.0453
Circuit | 024201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 79 | 1 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 1 | 0 | 8.2 | 0.21 | 39.75 | 0.9998 | 0.282
Circuit | 088202 |  |  |  |  | 1 | 1 |  |  | 10 | [6 empty] | 128 | 127 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4.5 | 0.08 | 58.43 | 0.9999 | 0.0114
Circuit | 042501 |  |  |  |  | 1 | 1 |  |  | 667 | [6 empty] | 2012 | 0 | 0 | 2002 | 0 | 0 | 9 | 1 | 0 | 0 | 0 | 1.07 | 0.01 | 212.68 | 1 | 0.1274
Circuit | 072902 |  |  |  |  | 1 | 1 |  |  | 163 | 2.8 |  |  | 25 | 0.11 | 0.11 | 164 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 25.88 | 0.15 | 168.03 | 0.9994
Circuit | 017302 |  |  | 0 |  | 1 |  | 1 |  | 0 | [6 empty] | 734 | 0 | 0 | 0 | 0 | 0 | 734 | 0 | 0 | 0 | 0 | 102.02 | 0.77 | 132.45 | 0.9976 | 1.1889
Circuit | 042102 |  |  |  |  | 1 | 1 |  |  | 35 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 418 | 1 | 0.0047
Circuit | 002703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0 | 139 | 1 | 0.0047
Circuit | 001302 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 3 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.42 | 0 | 169.07 | 1 | 0.0058
Circuit | 102601 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.35 | 0 | 258 | 1 | 0.9905
Circuit | 105302 | [30 empty] | 0.604
Circuit | 060803 | [8 empty] | 0
Circuit | 017602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.1 | 0 | 94.05 | 1 | 0.003
Circuit | 040302 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 83 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.82 | 0.06 | 167.15 | 0.9998 | 0.0495
Circuit | 077602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 38 | 0 | 1 | 0 | 0 | 0 | 35 | 0 | 1 | 1 | 0 | 6.34 | 0.05 | 128.3 | 0.9999 | 0.342
Circuit | 021902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 31 | 1 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 4.08 | 0.02 | 232.25 | 0.9999 | 0.0034
Circuit | 126702 |  |  |  |  | 1 |  | 1 |  | 1 | [6 empty] | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.12 | 0.01 | 201.9 | 1 | 0.7689
Circuit | 054402 | [8 empty] | 0 | [21 empty] | 0.0035
Circuit | 037001 |  |  | 0 |  | 1 | 1 |  |  | 0 | [6 empty] | 34 | 23 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 2.72 | 0.02 | 159.68 | 0.9999 | 0.001
Circuit | 124702 | [8 empty] | 0 | [21 empty] | 0.0079
Circuit | 050301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.06 | 0 | 127.25 | 1 | 0.0076
Circuit | 031102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 0 | 394 | 1
Circuit | 133203 | [8 empty] | 0 | [21 empty] | 0.0004
Circuit | 118302 | [8 empty] | 0
Circuit | 035102 | [8 empty] | 0 | [6 empty] | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0021
Circuit | 067202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 23 | 4.4 | 0.1 | 42.88 | 0.9999
Circuit | 076701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.27 | 0.2 | 101.85 | 0.9995 | 0.0047
Circuit | 154901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 8.71 | 0.1 | 87.26 | 0.9998 | 0.0016
Circuit | 004501 | [8 empty] | 2 | [21 empty] | 0.0019
Circuit | 039002 |  |  |  |  | 1 | 0 |  |  | 0 | 0.13 |  |  | 2.71 | 0.05 | 0.05 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.23 | 0 | 660 | 1 | 0.0019
Circuit | 076004
Circuit | 054002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.06 | 0 | 100.01 | 1 | 0.0689
Circuit | 000702 | [8 empty] | 0
Circuit | 023702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 22 | 7 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2.17 | 0.02 | 143.8 | 0.9999 | 0.0075
Circuit | 090302 | [8 empty] | 0 | [21 empty] | 0.1275
Circuit | 038102 |  |  |  |  | 1 | 1 |  |  | 0 | 0.51 |  |  | 0.42 | 1.2 | 1.05 | 225 | 2 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 147 | 7 | 17.49 | 0.14 | 127.89 | 0.9996 | 0.1343
Circuit | 134001 |  |  |  |  | 1 | 0.667 |  |  | 52 | [6 empty] | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1.38 | 0.01 | 236.67 | 1 | 0.0156
Circuit | 051102 | [30 empty] | 0.0407
Circuit | 042301 |  |  |  | 1 | 1 | 0 | 1 |  | 0 | [6 empty] | 2159 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2155 | 59.78 | 1.27 | 47.15 | 0.9986 | 0.8538
Circuit | 041102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1053 | 0 | 76.31 | 0.6 | 127.25 | 0.9982 | 0.1424
Circuit | 058606 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 144 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 142 | 3.93 | 0.07 | 56.03 | 0.9999 | 0.0506
Circuit | 151102 |  |  |  | 0.5 | 1 | 1 |  |  | 0 | [6 empty] | 21 | 1 | 0 | 0 | 0 | 18 | 1 | 0 | 0 | 1 | 0 | 5.81 | 0.02 | 353.31 | 0.9999 | 0.0071
Circuit | 072801 |  |  |  |  | 1 | 0.526 |  |  | 0 | [6 empty] | 57 | 29 | 0 | 0 | 0 | 0 | 27 | 1 | 0 | 0 | 0 | 26.16 | 0.07 | 374.93 | 0.9994 | 0.1236
Circuit | 003902 |  |  | 0 |  | 1 | 1 |  |  | 0 | 2.43 |  |  | 13.77 | 0.18 | 0.18 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 52 | 6.37 | 0.05 | 134.91 | 0.9999 | 0.0028
Circuit | 092001
Circuit | 067503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.19 | 0 | 78.15 | 1
Circuit | 061202 |  |  |  |  | 1 | 1 | 1 |  | 19 | [6 empty] | 19 | 1 | 0 | 0 | 0 | 0 | 17 | 0 | 1 | 0 | 0 | 7.08 | 0.03 | 237.87 | 0.9998 | 0.1489
Circuit | 043901 | [8 empty] | 0 | [21 empty] | 0.0635
Circuit | 121702 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7.33 | 0.08 | 96.06 | 0.9998 | 0.2312
Circuit | 060103 | [8 empty] | 0 | [21 empty] | 0.0026
Circuit | 001901 |  |  |  |  | 1 | 1 | 1 |  | 35 | [6 empty] | 70 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 55 | 2.49 | 0.04 | 55.82 | 0.9999 | 0.0026
Circuit | 154201 |  |  |  |  | 1 | 1 | 1 |  | 446 | 2.27 |  |  | 0 | 1 | 2.27 | 287 | 14 | 1 | 1 | 0 | 0 | 270 | 0 | 0 | 0 | 1 | 84.07 | 0.38 | 222.52 | 0.9981 | 0.1889
Circuit | 063502 | [8 empty] | 0 | [21 empty] | 2.5728
Circuit | 163503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.37 | 0.01 | 167.03 | 1 | 0.0033
Circuit | 097701 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.16 | 0 | 36.73 | 1 | 0.0647
Circuit | 023401 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 22 | 1 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 2.58 | 0.02 | 164.7 | 0.9999 | 0.2413
Circuit | 006107 | [8 empty] | 0
Circuit | 076902 | [8 empty] | 0
Circuit | 036004 | [8 empty] | 0
Circuit | 083501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 10 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1.41 | 0.01 | 246.1 | 1 | 0.0196
Circuit | 106503 | [8 empty] | 0 | [21 empty] | 0.0142
Circuit | 056901 | [8 empty] | 0 | [21 empty] | 0.0293
Circuit | 033801 |  |  |  | 1 | 1 | 1 |  |  | 1 | [6 empty] | 41 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 2.66 | 0.03 | 93.89 | 0.9999 | 0.1373
Circuit | 034401 |  |  |  |  | 1 | 1 | 1 |  | 35 | [6 empty] | 42 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 37 | 0 | 3.54 | 0.03 | 101.1 | 0.9999 | 0.0033
Circuit | 082002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.15 | 0 | 125 | 1
Circuit | 129301 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 57 | 0 | 2 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 6.29 | 0.06 | 111.09 | 0.9999 | 0.0933
Circuit | 033401 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56 | 0 | 577.18 | 1
Circuit | 110803 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 35 | 1 | 20 | 0 | 0 | 0 | 13 | 0 | 0 | 1 | 0 | 24.23 | 0.06 | 391.83 | 0.9994 | 0.0848
Circuit | 136601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7 | 0.43 | 0.01 | 73.12 | 1 | 0.0007
Circuit | 127502 | [8 empty] | 0 | [21 empty] | 0.1261
Circuit | 163102 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 325 | 23 | 1 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 43.87 | 0.37 | 117.71 | 0.999 | 0.8245
Circuit | 078301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.84 | 0.01 | 165.88 | 1
Circuit | 106502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1.01 | 0.01 | 76.04 | 1 | 0.0026
Circuit | 163703 |  |  | 1 |  | 1 | 1 | 1 |  | 185 | [6 empty] | 72 | 37 | 0 | 0 | 0 | 0 | 2 | 6 | 1 | 26 | 0 | 9.82 | 0.09 | 113.15 | 0.9998 | 0.0108
Circuit | 011701 | [15 empty] | 53 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Circuit | 095402 |  |  |  |  | 1 | 0.739 |  |  | 0 | [6 empty] | 299 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399.41 | 0.88 | 452.84 | 0.9908 | 0.0354
Circuit | 053502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 141 | 1 | 0.1433
Circuit | 010003
Circuit | 029201 |  |  |  |  | 1 |  | 1 |  | 99 | [6 empty] | 107 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 26.13 | 0.23 | 114.23 | 0.9994 | 4.1132
Circuit | 091802 |  |  | 1 |  | 1 | 1 | 1 |  | 238 | [6 empty] | 273 | 98 | 26 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1 | 77.88 | 0.61 | 128.66 | 0.9982 | 0.4368
Circuit | 148502 | [8 empty] | 0
Circuit | 121701 | [8 empty] | 0 | [21 empty] | 0.0024
Circuit | 024302 |  |  | 1 | [5 empty] | 0 | [21 empty] | 0.2199
Circuit | 030501 |  |  |  |  | 1 | 1 |  |  | 509 | [6 empty] | 1749 | 19 | 0 | 1672 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 8.27 | 0.1 | 86.14 | 0.9998 | 0.3055
Circuit | 039003 |  |  | 0 |  | 1 | 1 |  |  | 0 | 0 |  |  | 11.3 | 0 | 0.22 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81 | 0.02 | 46.04 | 1 | 0.0277
Circuit | 070103 | [30 empty] | 0.6667
Circuit | 070802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 5.35 | 0.01 | 373.49 | 0.9999 | 0.0018
Circuit | 011202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 279 | 1 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 258 | 71.15 | 0.73 | 96.91 | 0.9984 | 0.3211
Circuit | 125102 | [8 empty] | 0 | [21 empty] | 0.9486
Circuit | 099202 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 117.84 | 1.01 | 116.47 | 0.9973 | 0.6765
Circuit | 031201 |  |  |  | 1 | 1 | 1 | 1 |  | 0 | [6 empty] | 348 | 39 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 39 | 1 | 62.22 | 0.47 | 131.06 | 0.9986 | 0.8008
Circuit | 010929
Circuit | 024404 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.23 | 0 | 113 | 1 | 0.004
Circuit | 040601 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 182 | 1 | 0 | 0 | 0 | 0 | 180 | 0 | 1 | 0 | 0 | 19.62 | 0.26 | 76.33 | 0.9995 | 3.4266
Circuit | 024203
Circuit | 072901 |  |  |  |  | 1 | 1 |  |  | 122 | [6 empty] | 350 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.03 | 0.19 | 91 | 0.9996 | 0.3016
Circuit | 072402 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.28 | 0 | 233.77 | 1 | 0.075
Circuit | 099802 | [8 empty] | 0 | [21 empty] | 0.0038
Circuit | 127003 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 30 | 1 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 2.85 | 0.03 | 84.43 | 0.9999 | 0.0056
Circuit | 060102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 52 | 1 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 11.09 | 0.09 | 120.92 | 0.9997 | 0.0935
Circuit | 070801 |  |  |  |  | 1 | 0.695 | 1 |  | 0 | [6 empty] | 252 | 140 | 0 | 0 | 0 | 0 | 6 | 0 | 42 | 64 | 0 | 42.91 | 0.15 | 287.45 | 0.999
Circuit | 000901 |  |  |  |  | 1 | 1 | 1 |  | 0 | 0 |  |  | 22.8 | 0 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.27 | 0 | 81.63 | 1
Circuit | 082401 | [8 empty] | 0
Circuit | 092302 | [9 empty] | 0 |  |  | 1.07 | 0 | 0 | [15 empty] | 0.0667
Circuit | 168903
Circuit | 135901 |  |  |  |  | 1 | 1 |  |  | 779 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.12 | 0 | 96.22 | 1 | 1.1667
Circuit | 041603 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1.08 | 0.01 | 78.16 | 1 | 0.0028
Circuit | 137804 |  |  |  |  | 1 | 1 | 1 |  | 1 | 0 |  |  | 0 | 0 | 0.25 | 24 | 0 | 1 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 1.99 | 0.02 | 121.52 | 1 | 0.1237
Circuit | 023103 | [8 empty] | 0 | [21 empty] | 0.006
Circuit | 127301 |  |  |  |  | 1 | 0.8 |  |  | 0 | 1.62 |  |  | 0 | 1 | 1.9 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3.15 | 0.01 | 516.67 | 0.9999 | 0.581
Circuit | 057602 |  |  |  |  | 1 | 1 |  |  | 560 | [6 empty] | 63 | 49 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 5.84 | 0.05 | 129.14 | 0.9999 | 0.2635
Circuit | 057501 | [8 empty] | 0 | [21 empty] | 0.1394
Circuit | 163101 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0.55 | 0 | 0.97 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0.43 | 0.02 | 23.8 | 1 | 0.0203
Circuit | 101901 | [8 empty] | 0
Circuit | 095202 |  |  |  |  | 1 | 1 | 1 |  | 267 | [6 empty] | 23 | 1 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 16 | 0 | 1.72 | 0.03 | 53.71 | 1 | 0.0084
Circuit | 034001 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 64 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 5.59 | 0.05 | 108.95 | 0.9999 | 0.0858
Circuit | 057802 |  |  | 1 |  | 1 | 0.333 |  |  | 10 | [6 empty] | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.78 | 0 | 726.01 | 1 | 0.0041
Circuit | 120201 |  |  | 1 | [5 empty] | 0 | [21 empty] | 0.0071
Circuit | 114702 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 68.7 | 1 | 0.0773
Circuit | 021701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1556 | 1556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403.27 | 1.02 | 396.53 | 0.9907 | 1.0359
Circuit | 021802 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 12 | 1 | 0.0038
Circuit | 071202 |  |  |  |  | 1 | 0.719 |  |  | 2 | [6 empty] | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 3.99 | 0.02 | 227.92 | 0.9999 | 0.0038
Circuit | 036202 |  |  |  | 1 |  |  |  |  | 0 | [21 empty] | 0.0016
Circuit | 077001 | [8 empty] | 0 | [21 empty] | 0.1929
Circuit | 051602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 39.57 | 0.29 | 135.01 | 0.9991 | 0.0172
Circuit | 167404 | [30 empty] | 0.0352
Circuit | 008503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1.63 | 0.02 | 84.52 | 1 | 0.0044
Circuit | 100902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 317 | 284 | 25 | 0 | 0 | 0 | 1 | 0 | 0 | 7 | 0 | 39.48 | 0.33 | 119.42 | 0.9991 | 0.6559
Circuit | 073602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.18 | 0 | 81.91 | 1 | 0.0011
Circuit | 041104 | [8 empty] | 0 | [21 empty] | 0.0102
Circuit | 050802 | [8 empty] | 0 | [21 empty] | 0.0015
Circuit | 101204 | [9 empty] | 0 |  |  | 0 | 0 | 1
Circuit | 121002 | [9 empty] | 0 |  |  | 0 | 0 | 1 | [15 empty] | 0.0013
Circuit | 041302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 1.45 | 0.01 | 137.38 | 1 | 0.0029
Circuit | 076606 | [8 empty] | 0 | [21 empty] | 0.003
Circuit | 002702 |  |  |  | 1 | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.32 | 0 | 142 | 1
Circuit | 056902 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.55 | 0 | 733 | 1
Circuit | 136001 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 2.75 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0 | 151.53 | 1 | 0.6987
Circuit | 076005 | [8 empty] | 0
Circuit | 148302 | [30 empty] | 0.0028
Circuit | 158202 |  |  |  | 0 | 1 | 0.172 | 1 |  | 0 | [6 empty] | 278 | 1 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 1 | 0 | 105.31 | 0.21 | 501.15 | 0.9976 | 0.0015
Circuit | 061805 | [8 empty] | 0
Circuit | 111206
Circuit | 030202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 58 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 3 | 0 | 1 | 13.9 | 0.06 | 217.64 | 0.9997 | 0.2731
Circuit | 053501 | [8 empty] | 0 | [21 empty] | 0.0018
Circuit | 035202 | [8 empty] | 0 | [21 empty] | 0.2435
Circuit | 039802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.54 | 0 | 182.31 | 1 | 0.0235
Circuit | 003901 |  |  |  |  | 1 | 1 |  |  | 229 | 0.82 |  |  | 0.82 | 1 | 1 | 1820 | 32 | 0 | 0 | 0 | 26 | 0 | 58 | 0 | 1671 | 33 | 140.51 | 1.05 | 134.18 | 0.9967 | 0.0575
Circuit | 007302 |  |  |  |  | 1 | 1 |  |  | 0 | 0.32 |  |  | 1.48 | 0.21 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0 | 253.38 | 1 | 0.0453
Circuit | 003803 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 1.4 | 0.01 | 175.33 | 1
Circuit | 041003 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 101 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 0 | 5.32 | 0.08 | 63.92 | 0.9999 | 0.0124
Circuit | 141202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.06 | 0 | 65 | 1
Circuit | 057402 |  |  |  |  | 1 | 0.953 | 1 |  | 0 | 13.56 |  |  | 41.97 | 0.32 | 0.76 | 65 | 4 | 0 | 0 | 0 | 0 | 59 | 0 | 1 | 1 | 0 | 7.07 | 0.03 | 249.27 | 0.9998 | 1.1784
Circuit | 019603 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1.64 | 0.04 | 39.31 | 1 | 0.0017
Circuit | 090103 | [30 empty] | 0.0054
Circuit | 130302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 71 | 0 | 0 | 0 | 0 | 70 | 1 | 0 | 0 | 0 | 0 | 10.16 | 0.05 | 202.6 | 0.9998 | 0.0035
Circuit | 096202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 276 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.52 | 0.32 | 164.61 | 0.9988 | 0.0046
Circuit | 100502 |  |  |  |  | 1 | 0.983 |  |  | 0 | [6 empty] | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 2 | 0 | 18.27 | 0.07 | 280.05 | 0.9996 | 1.0326
Circuit | 065403
Circuit | 035701 | [30 empty] | 0.0214
Circuit | 125202 | [8 empty] | 0 | [21 empty] | 0.0026
Circuit | 074301 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 142 | 126 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 6 | 18.5 | 0.12 | 156.69 | 0.9996 | 0.6367
Circuit | 032202 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 31 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 1 | 0 | 0 | 6.32 | 0.04 | 179.48 | 0.9999 | 0.0023
Circuit | 060701 | [8 empty] | 0 | [21 empty] | 0.0951
Circuit | 041001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.44 | 0 | 285.19 | 1 | 0.0023
Circuit | 098205 | [8 empty] | 0
Circuit | 052302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 865 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.83 | 1.28 | 18.6 | 0.9994 | 0.0785
Circuit | 025402 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.83 | 0 | 299 | 1 | 0.0028
Circuit | 060201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.62 | 0 | 199.6 | 1
Circuit | 086802 |  |  |  |  | 1 | 1 |  |  | 10 | [6 empty] | 24 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 1 | 0 | 7.34 | 0.03 | 237.38 | 0.9998 | 0.0013
Circuit | 064702 | [8 empty] | 0 | [21 empty] | 0.0087
Circuit | 072601 | [8 empty] | 0 | 2.06 |  |  | 2.07 | 0.99 | 1
Circuit | 039201 | [8 empty] | 0 | [21 empty] | 0.002
Circuit | 076006 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 18 | 7 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 1.93 | 0.01 | 184.43 | 1 | 0.0006
Circuit | 069803 |  |  |  |  | 1 | 0.833 |  |  | 0 | 0 |  |  | 0.88 | 0 | 0.56 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 0 | 265.75 | 1 | 0.0015
Circuit | 078902 |  |  |  |  | 1 | 0.8 | 1 |  | 0 | [6 empty] | 6 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1.25 | 0.01 | 206.92 | 1 | 0.4403
Circuit | 067501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.24 | 0 | 149.26 | 1
Circuit | 076002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.07 | 0 | 79.1 | 1 | 0.0175
Circuit | 066801 | [8 empty] | 0
Circuit | 070202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 94 | 1 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 16.76 | 0.11 | 150.8 | 0.9996 | 0.1749
Circuit | 024502 | [8 empty] | 0 | [21 empty] | 0.0036
Circuit | 057401 |  |  |  |  | 1 | 0.167 |  |  | 0 | 4.86 |  |  | 6.15 | 0.79 | 0.96 | 6 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5.02 | 0.01 | 499.82 | 0.9999 | 0.9347
Circuit | 045702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 1.97 | 0.02 | 128.27 | 1
Circuit | 002303 |  |  | 1 |  | 1 | 0 |  |  | 3 | 0 |  |  | 10.12 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.24 | 0 | 531.64 | 1 | 0.01
Circuit | 076401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.29 | 0 | 237 | 1 | 0.11
Circuit | 128401 | [8 empty] | 0 | [21 empty] | 0.0044
Circuit | 010704
Circuit | 136805 | [8 empty] | 0 | [21 empty] | 0.001
Circuit | 083503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.16 | 0 | 69.75 | 1 | 0.0078
Circuit | 030601 | [8 empty] | 0 | [21 empty] | 0.0812
Circuit | 076510
Circuit | 016202 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 183 | 0 | 126.01 | 0.75 | 167.07 | 0.9971 | 0.0454
Circuit | 147303 | [30 empty] | 0.0033
Circuit | 128002 | [8 empty] | 1
Circuit | 124203 | [8 empty] | 0 | [21 empty] | 0.0019
Circuit | 115702 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 18 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 1 | 8.79 | 0.09 | 99.17 | 0.9998 | 0.8966
Circuit | 129603 | [8 empty] | 0 | [21 empty] | 0.0011
Circuit | 135905
Circuit | 134802 | [8 empty] | 0 | [21 empty] | 0.0018
Circuit | 154602 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.69 | 0 | 353 | 1 | 0.0049
Circuit | 107501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0 | 110.44 | 1
Circuit | 049602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 61 | 1 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 6.24 | 0.08 | 77.38 | 0.9999 | 0.0026
Circuit | 042304 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 0 | 327 | 1
Circuit | 039601 |  |  |  |  | 1 | 0.959 |  |  | 0 | [6 empty] | 49 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 1 | 0 | 0 | 8.63 | 0.04 | 199.39 | 0.9998 | 0.0698
Circuit | 040901 |  |  |  |  | 1 | 0.25 |  |  | 0 | [6 empty] | 4 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 2.38 | 0 | 599.75 | 0.9999 | 0.001
Circuit | 082903 | [30 empty] | 0.0043
Circuit | 072702
Circuit | 098201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.43 | 0.02 | 137.56 | 0.9999
Circuit | 022504 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 18 | 0 | 2.39 | 0.02 | 126.67 | 0.9999 | 0.002
Circuit | 134803 |  |  | 1
Circuit | 031202 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 201 | 1 | 186 | 0 | 0 | 0 | 1 | 11 | 0 | 0 | 2 | 64.21 | 0.25 | 253.32 | 0.9985 | 0.5032
Circuit | 063401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.27 | 0 | 95 | 1
Circuit | 042402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.1 | 0 | 63 | 1 | 0.9791
Circuit | 031801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0 | 166.11 | 1 | 0.0011
Circuit | 023002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 1.64 | 0.01 | 140.87 | 1 | 0.0116
Circuit | 005701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 303 | 1 | 0.0025
Circuit | 030602 | [8 empty] | 0 | [21 empty] | 0.0052
Circuit | 050502 | [8 empty] | 0 | [21 empty] | 3.0211
Circuit | 151602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 92 | 0 | 0 | 0 | 1 | 0 | 91 | 0 | 0 | 0 | 0 | 14.87 | 0.15 | 101.66 | 0.9997 | 0.221
Circuit | 007304 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.12 | 0 | 109 | 1 | 0.0192
Circuit | 067401 | [8 empty] | 0
Circuit | 063302 | [8 empty] | 0 | [21 empty] | 0.0053
Circuit | 139501 |  |  |  |  | 1 | 1 | 1 |  | 655 | [6 empty] | 462 | 2 | 277 | 0 | 0 | 0 | 62 | 0 | 121 | 0 | 0 | 29.7 | 0.26 | 115.21 | 0.9993 | 0.1825
Circuit | 021203 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.08 | 0 | 106.01 | 1 | 0.8852
Circuit | 129401 |  |  |  |  | 1 | 0.509 | 1 |  | 104 | [6 empty] | 250 | 0 | 1 | 0 | 0 | 0 | 167 | 0 | 1 | 0 | 81 | 27.23 | 0.09 | 294.93 | 0.9994 | 0.031
Circuit | 133904 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 1.12 | 0.01 | 162.67 | 1 | 0.0069
Circuit | 080801 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 53 | 0 | 0 | 0 | 0 | 0 | 45 | 1 | 0 | 1 | 6 | 29.17 | 0.15 | 196.51 | 0.9993 | 0.3053
Circuit | 107603 | [8 empty] | 0 | [21 empty] | 0.0019
Circuit | 074901 | [8 empty] | 0
Circuit | 093201 | [8 empty] | 0 | [21 empty] | 0.002
Circuit | 054101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 13 | 12 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3.89 | 0.02 | 239.58 | 0.9999
Circuit | 102902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0 | 156 | 1 | 0.0015
Circuit | 078702 |  |  |  |  | 1 |  | 1 |  | 1 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.46 | 0 | 177.5 | 1 | 0.0026
Circuit | 010910
Circuit | 008506 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.46 | 0.02 | 113 | 0.9999
Circuit | 149301 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 3.85 | 0 | 0 | 18 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 3.34 | 0.05 | 61.41 | 0.9999 | 0.0242
Circuit | 023001 | [8 empty] | 0 | [21 empty] | 0.0058
Circuit | 050902 | [8 empty] | 1014 | [6 empty] | 1019 | 0 | 0 | 1019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0156
Circuit | 109101 | [8 empty] | 786 | [6 empty] | 443 | 0 | 0 | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.2659
Circuit | 063101 |  |  |  |  | 1 | 0.944 | 1 |  | 0 | [6 empty] | 38 | 0 | 3 | 0 | 0 | 0 | 34 | 1 | 0 | 0 | 0 | 15.7 | 0.04 | 438.85 | 0.9996 | 0.2194
Circuit | 037502 |  |  |  | 0 | 1 | 0.935 |  |  | 268 | [6 empty] | 46 | 1 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 2 | 0 | 19.62 | 0.09 | 228.15 | 0.9995 | 0.1009
Circuit | 029301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 36 | 2 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 3.81 | 0.02 | 251.73 | 0.9999 | 0.0021
Circuit | 060902 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37 | 0 | 142.5 | 1
Circuit | 112503 |  |  | 1 |  | 1 | 0.093 |  |  | 3 | [6 empty] | 54 | 1 | 0 | 0 | 0 | 0 | 0 | 49 | 3 | 1 | 0 | 37.22 | 0.04 | 892.61 | 0.9991 | 1.1027
Circuit | 037302 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 139 | 14 | 0 | 0 | 0 | 0 | 122 | 2 | 0 | 1 | 0 | 16.1 | 0.1 | 161.02 | 0.9996 | 1.7237
Circuit | 014601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.05 | 0 | 101.44 | 1 | 0.0019
Circuit | 158201 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 18 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.91 | 0.01 | 85.54 | 1
Circuit | 063603 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 49 | 1 | 1 | 0 | 0 | 0 | 0 | 15 | 0 | 32 | 0 | 4.78 | 0.03 | 172.85 | 0.9999 | 0.1196
Circuit | 014802 |  |  |  |  | 1 | 1 |  |  | 38 | [6 empty] | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 2.84 | 0.16 | 18.28 | 0.9999 | 0.005
Circuit | 032402 |  |  |  |  | 1 | 1 |  |  | 13 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.29 | 0 | 97 | 1 | 1.7238
Circuit | 004504 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 80 | 5 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 13.3 | 0.05 | 244.38 | 0.9997 | 0.002
Circuit | 155801 |  |  | 0.5 |  | 1 | 0.4 |  |  | 2 | [6 empty] | 5 | 1 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 1.74 | 0 | 369.86 | 1 | 0.0151
Circuit | 026802 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 90 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 1 | 0 | 0 | 19.96 | 0.14 | 143.71 | 0.9995 | 0.0046
Circuit | 039801 | [8 empty] | 0 | [21 empty] | 0.0023
Circuit | 018001 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 3 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.69 | 0.01 | 440.29 | 0.9999 | 0.5967
Circuit | 162002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 39 | 1 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16.9 | 0.08 | 209.34 | 0.9996 | 0.0228
Circuit | 029501 |  |  |  |  | 1 | 1 |  |  | 23 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0 | 350 | 1 | 0.0129
Circuit | 088203 |  |  |  |  | 1 | 0.947 |  |  | 1 | [6 empty] | 19 | 16 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 2.76 | 0.02 | 157.65 | 0.9999 | 0.5963
Circuit | 077201 |  |  |  |  | 1 | 1 |  |  | 50 | [6 empty] | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 14.58 | 0.1 | 151.05 | 0.9997 | 0.3018
Circuit | 033102
Circuit | 063403 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.48 | 0.01 | 110 | 1 | 0.985
Circuit | 080302 | [30 empty] | 0.0106
Circuit | 048901 | [8 empty] | 0 | [21 empty] | 0.5135
Circuit | 039402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 0.01 | 92.35 | 1 | 0.1554
Circuit | 125201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 188 | 1 | 0.0934
Circuit | 049101 |  |  |  |  | 1 | 1 |  |  | 10 | 7.77 |  |  | 15.19 | 0.51 | 0.58 | 16 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 6 | 3.49 | 0.03 | 110.63 | 0.9999 | 0.002
Circuit | 033701 | [8 empty] | 0 | 6.72 |  |  | 6.62 | 1.01 | 1.01
Circuit | 032504 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 106 | 1 | 0.001
Circuit | 032301 | [8 empty] | 0 | [21 empty] | 0.0023
Circuit | 082901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.15 | 0 | 95 | 1
Circuit | 106602
Circuit | 037603 |  |  |  |  | 1 | 1 |  |  | 84 | [6 empty] | 4 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.63 | 0 | 200.19 | 1 | 0.2136
Circuit | 030902 |  |  |  |  | 1 | 1 | 1 |  | 192 | [6 empty] | 379 | 273 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 66 | 0 | 116.45 | 0.78 | 148.41 | 0.9973 | 0.7474
Circuit | 067403 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 0 | 6.38 | 0.04 | 164.69 | 0.9999 | 0.0052
Circuit | 160402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 87 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.86 | 0.13 | 385.81 | 0.9988 | 0.0061
Circuit | 000705 |  |  | 1 | [6 empty] | 0 |  |  | 6.95 | 0 | 0 | [15 empty] | 0.002
Circuit | 045401 | [30 empty] | 0.72
Circuit | 024403 | [8 empty] | 0 | [21 empty] | 0.0021
Circuit | 066302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 60 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 41 | 5.92 | 0.04 | 143.25 | 0.9999 | 0.0709
Circuit | 006108
Circuit | 004503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 2.94 | 0.04 | 75.53 | 0.9999
Circuit | 022901 |  |  |  |  | 1 | 1 | 1 |  | 136 | [6 empty] | 51 | 49 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 7.44 | 0.05 | 160.12 | 0.9998 | 0.1568
Circuit | 101902 | [8 empty] | 0 | [21 empty] | 0.0052
Circuit | 151101
Circuit | 025302 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 60 | 1 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51 | 0 | 671 | 1 | 0.0788
Circuit | 050103 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25.48 | 0.01 | 1965.38 | 0.9994 | 0.0026
Circuit | 032501 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 1268 | 0 | 1224 | 2 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 167.69 | 0.86 | 195.77 | 0.9961 | 0.0217
Circuit | 028301 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 47 | 1 | 0 | 0 | 0 | 0 | 43 | 0 | 3 | 0 | 0 | 2.31 | 0.02 | 108.47 | 0.9999 | 0.0054
Circuit | 059901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 21.09 | 0.11 | 191.69 | 0.9995 | 0.0763
Circuit | 028903 |  |  |  |  | 1 | 0.99 |  |  | 0 | [6 empty] | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 17.51 | 1.02 | 17.14 | 0.9996 | 0.1277
Circuit | 056301 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 11.59 | 0.02 | 767.72 | 0.9997 | 0.005
Circuit | 063201
Circuit | 012701 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0 | 238.79 | 1 | 0.008
Circuit | 022503 | [8 empty] | 0 | [21 empty] | 0.0067
Circuit | 103102 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 4 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0.01 | 199.88 | 1 | 0.018
Circuit | 054804 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.53 | 0.06 | 40.9 | 0.9999 | 0.0018
Circuit | 072703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0.94 | 0.01 | 64.18 | 1
Circuit | 115005
Circuit | 021602 |  |  |  |  | 1 | 0.333 |  |  | 0 | [6 empty] | 6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 4.57 | 0.01 | 410.41 | 0.9999 | 0.0037
Circuit | 167302 | [8 empty] | 0
Circuit | 150102
Circuit | 032001 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2.05 | 0.03 | 78.07 | 1 | 0.0044
Circuit | 136801 | [8 empty] | 0 | [21 empty] | 0.0005
Circuit | 150902 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.04 | 0 | 350 | 1 | 0.4821
Circuit | 041802 |  |  |  |  | 1 | 1 |  |  | 382 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.49 | 0 | 317 | 1
Circuit | 102201 |  |  |  |  | 1 | 1 | 1 |  | 0 | 8.18 |  |  | 22.74 | 0.36 | 0.36 | 64 | 0 | 2 | 0 | 0 | 17 | 42 | 0 | 0 | 3 | 0 | 9.68 | 0.09 | 106.62 | 0.9998 | 0.1206
Circuit | 091603 | [8 empty] | 2 | [21 empty] | 0.015
Circuit | 025502 |  |  | 1 |  | 1 | 1 | 0.962 |  | 0 | [6 empty] | 920 | 682 | 1 | 55 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 162.88 | 1.26 | 128.99 | 0.9962 | 0.2321
Circuit | 011702 | [8 empty] | 0 | [21 empty] | 0.0067
Circuit | 149802 | [8 empty] | 0 | 2.04 |  |  | 2.05 | 1 | 1 | [15 empty] | 0.0022
Circuit | 044202 | [8 empty] | 0 | [21 empty] | 0.22
Circuit | 030002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74 | 0 | 229.97 | 1 | 0.4595
Circuit | 036902 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 6.02 | 0.01 | 677.74 | 0.9999 | 0.003
Circuit | 005402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 86 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.61 | 0.06 | 57.44 | 0.9999 | 0.0044
Circuit | 151201 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0.08 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.1 | 0 | 123 | 1
Circuit | 121003 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0.95 | 0.02 | 59.05 | 1 | 0.0011
Circuit | 010001 |  |  | 1 |  | 1 | 0.857 |  |  | 0 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0.54 | 0 | 203.45 | 1 | 0.0075
Circuit | 100602 | [8 empty] | 0
Circuit | 053404 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 108 | 1 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 5 | 0 | 23.1 | 0.17 | 132.6 | 0.9995 | 1.1242
Circuit | 060903 |  |  |  |  | 1 | 1 |  |  | 801 | [6 empty] | 812 | 0 | 0 | 0 | 0 | 0 | 812 | 0 | 0 | 0 | 0 | 189.81 | 0.95 | 198.93 | 0.9956 | 0.0552
Circuit | 098204 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 0.6
Circuit | 120202 | [8 empty] | 0 | [21 empty] | 0.0018
Circuit | 061802
Circuit | 009201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.23 | 0 | 172.99 | 1 | 1.0664
Circuit | 006703 | [9 empty] | 0.16 |  |  | 0 | 1 | 1.04
Circuit | 162201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1.56 | 0.01 | 166.74 | 1 | 0.0237
Circuit | 074304 | [9 empty] | 0.45 |  |  | 5.11 | 0.09 | 0.3 | [15 empty] | 0.0019
Circuit | 137003 | [8 empty] | 0
Circuit | 090003 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.66 | 0 | 135.46 | 1 | 0.0098
Circuit | 109802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.28 | 0 | 289 | 1 | 0.0297
Circuit | 056903 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 0 | 47 | 1
Circuit | 012001 | [30 empty] | 0.0029
Circuit | 025201 | [8 empty] | 0 | [21 empty] | 0.0013
Circuit | 033702 | [8 empty] | 0 | [21 empty] | 0.0336
Circuit | 129402 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 14 | 2 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 4.39 | 0.02 | 283.64 | 0.9999
Circuit | 081503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.59 | 0 | 152.33 | 1
Circuit | 040702 |  |  |  |  | 1 | 0.964 |  |  | 259 | 5.65 |  |  | 0.31 | 18.21 | 1.88 | 137 | 2 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 32.62 | 0.09 | 358.78 | 0.9992 | 0.079
Circuit | 048601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.13 | 0 | 74.11 | 1 | 0.967
Circuit | 095201 | [8 empty] | 0 | [21 empty] | 0.0703
Circuit | 030502 |  |  |  |  | 1 | 1 | 1 |  | 215 | [6 empty] | 163 | 39 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 13.07 | 0.18 | 73.84 | 0.9997 | 0.0034
Circuit | 040801 | [8 empty] | 0 | [21 empty] | 0.0049
Circuit | 026901 | [8 empty] | 0
Circuit | 087702 | [8 empty] | 0 | [21 empty] | 0.0072
Circuit | 108102 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1.82 | 0.01 | 233.24 | 1 | 1.1328
Circuit | 076602 | [30 empty] | 0.0297
Circuit | 010914 | [9 empty] | 0 |  |  | 0 | 0 | 0
Circuit | 040502 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.75 | 0 | 393.5 | 1 | 0.0066
Circuit | 104405 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 236 | 1 | 0.0011
Circuit | 157404 |  |  |  |  | 1 | 0.5 | 1 |  | 0 | [6 empty] | 143 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17 | 0 | 17.47 | 0.11 | 154.3 | 0.9996 | 0.1259
Circuit | 017501 | [8 empty] | 0
Circuit | 029103 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.56 | 0 | 142.32 | 1 | 0.0488
Circuit | 149803 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 10 | 1 | 0.0013
Circuit | 097302 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 57 | 0 | 0 | 0 | 0 | 0 | 56 | 1 | 0 | 0 | 0 | 4.67 | 0.04 | 117.68 | 0.9999 | 0.0544
Circuit | 107203 |  |  |  |  | 1 | 1 | 1 |  | 247 | [6 empty] | 21 | 1 | 2 | 0 | 0 | 0 | 17 | 0 | 1 | 0 | 0 | 5.66 | 0.06 | 102.51 | 0.9999 | 0.0026
Circuit | 122703 | [30 empty] | 0.0079
Circuit | 123102 |  |  |  |  | 1 | 1 | 1 |  | 536 | [6 empty] | 1080 | 1 | 0 | 0 | 0 | 0 | 1079 | 0 | 0 | 0 | 0 | 142.72 | 2.71 | 52.59 | 0.9967 | 1.6935
Circuit | 149002 | [8 empty] | 0 | [21 empty] | 0.0014
Circuit | 119101 | [8 empty] | 0
Circuit | 028801 | [8 empty] | 10
Circuit | 057002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 22 | 1 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | 16 | 0 | 2.83 | 0.02 | 142.83 | 0.9999 | 0.0027
Circuit | 029801 |  |  |  |  | 1 | 1 |  |  | 12 | [6 empty] | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 0.01 | 128.85 | 1 | 0.8823
Circuit | 049301 | [8 empty] | 0 | [21 empty] | 0.0039
Circuit | 010902 | [30 empty] | 0.0133
Circuit | 086002 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0016
Circuit | 119201
Circuit | 041402 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 131 | 1 | 97 | 0 | 0 | 32 | 0 | 0 | 0 | 1 | 0 | 10.9 | 0.09 | 124.91 | 0.9997 | 0.0653
Circuit | 002701 | [30 empty] | 0.0025
Circuit | 046501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1996 | 0 | 0 | 0 | 0 | 0 | 0 | 1995 | 1 | 0 | 0 | 356.15 | 2.58 | 138.11 | 0.9918 | 4.6718
Circuit | 163601 | [30 empty] | 0.0288
Circuit | 090102 |  |  |  |  | 1 | 0.964 | 1 |  | 0 | [6 empty] | 42 | 9 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 6.25 | 0.03 | 196.72 | 0.9999 | 0.1368
Circuit | 049905 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0.16 | 0 | 115 | 1 | 0.0005
Circuit | 027502 | [8 empty] | 6 | [21 empty] | 0.0068
Circuit | 149801 | [8 empty] | 0
Circuit | 004801 |  |  |  |  | 1 | 1 |  |  | 78 | [6 empty] | 18 | 2 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 0 | 319.5 | 1 | 0.178
Circuit | 048302 | [8 empty] | 0 | [21 empty] | 0.9754
Circuit | 024801 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 151 | 0 | 127 | 0 | 0 | 0 | 23 | 0 | 0 | 1 | 0 | 6.32 | 0.06 | 112.13 | 0.9999 | 0.3595
Circuit | 063902 | [8 empty] | 0 | [21 empty] | 0.9451
Circuit | 070004 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 19 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2.28 | 0.02 | 115.42 | 0.9999 | 0.132
Circuit | 031001 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 393 | 1 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 221.2 | 0.7 | 314.63 | 0.9949 | 0.1682
Circuit | 009801 | [8 empty] | 0
Circuit | 157002 | [8 empty] | 0 | 0 |  |  | 0.24 | 0 | 0.5 | [15 empty] | 0.113
Circuit | 147802 |  |  | 1 | [5 empty] | 0 | [21 empty] | 0.9757
Circuit | 013401 | [8 empty] | 0
Circuit | 079301 | [8 empty] | 6 | [21 empty] | 0.0008
Circuit | 090503
Circuit | 021402 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.02 | 0 | 32 | 1 | 0.0008
Circuit | 006101
Circuit | 112603 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.14 | 0 | 203 | 1
Circuit | 049801 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 7 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.69 | 0.01 | 740.78 | 0.9999 | 0.0055
Circuit | 009203 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.56 | 0 | 596 | 1 | 1.0408
Circuit | 053102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 174 | 0 | 0 | 0 | 0 | 0 | 138 | 36 | 0 | 0 | 0 | 29.31 | 0.24 | 124.64 | 0.9993 | 0.0095
Circuit | 102101 |  |  |  |  | 1 | 0.033 |  |  | 0 | [6 empty] | 30 | 29 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.47 | 0.05 | 981.05 | 0.9989 | 0.0919
Circuit | 007102 | [8 empty] | 0 | [21 empty] | 0.0012
Circuit | 103503 | [30 empty] | 0.005
Circuit | 168603 | [8 empty] | 0
Circuit | 078002 | [8 empty] | 0 | [21 empty] | 0.0069
Circuit | 012401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 192 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.28 | 0.21 | 185.8 | 0.9991 | 0.1459
Circuit | 041604 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.74 | 0 | 312.2 | 1
Circuit | 122402 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 8.08 | 0.02 | 512.95 | 0.9998 | 0.0014
Circuit | 150001 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 986 | 0 | 319 | 0 | 0 | 0 | 667 | 0 | 0 | 0 | 0 | 52.98 | 0.51 | 104.62 | 0.9988 | 1.7458
Circuit | 075401 | [8 empty] | 38 | [21 empty] | 0.0012
Circuit | 061901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.11 | 0 | 93.45 | 1 | 0.0023
Circuit | 107601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 56 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.56 | 0.06 | 96.19 | 0.9999 | 0.13
Circuit | 046502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.25 | 0 | 148 | 1
Circuit | 154101 |  |  | 1 | [5 empty] | 0 | 0.39 |  |  | 0.93 | 0.42 | 0.42 | [15 empty] | 0.0019
Circuit | 099102 | [8 empty] | 0 | [21 empty] | 0.7645
Circuit | 131202 | [8 empty] | 0 | [21 empty] | 0.0101
Circuit | 032801 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 49 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 27 | 0 | 8.51 | 0.06 | 135.18 | 0.9998 | 0.4113
Circuit | 064705 | [8 empty] | 0 | [21 empty] | 0.1011
Circuit | 109801 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 187 | 1 | 0.0272
Circuit | 040903 |  |  | 0 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 24 | 1 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 1 | 0 | 25.36 | 0.12 | 208.17 | 0.9994 | 0.7766
Circuit | 017701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.27 | 0 | 161.1 | 1
Circuit | 055702 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 1.42 | 0.01 | 127.9 | 1 | 1.1981
Circuit | 065501 | [30 empty] | 1.2554
Circuit | 107202 |  |  |  |  | 1 | 1 | 1 |  | 280 | [6 empty] | 401 | 176 | 1 | 0 | 0 | 0 | 49 | 0 | 175 | 0 | 0 | 70.36 | 0.49 | 142.83 | 0.9984 | 0.3624
Circuit | 053002 | [8 empty] | 0 | 1.88 |  |  | 5.98 | 0.32 | 1 | [15 empty] | 0.0568
Circuit | 058202 |  |  |  |  | 1 |  | 1 |  | 0 | 0 |  |  | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.16 | 0 | 246.99 | 1 | 0.0032
Circuit | 127404 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0 | 172 | 1 | 0.0009
Circuit | 005702 | [8 empty] | 0 | [21 empty] | 0.0144
Circuit | 058102 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 0.46 | [15 empty] | 0.0102
Circuit | 112003 | [8 empty] | 0 | 0 |  |  | 0.72 | 0 | 0.5 | [15 empty] | 0.0016
Circuit | 151903
Circuit | 058802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 1 | 0 | 0 | 10.5 | 0.07 | 147.15 | 0.9998 | 0.0037
Circuit | 054001 | [8 empty] | 0 | [21 empty] | 0.0042
Circuit | 058003 | [30 empty] | 0.0009
Circuit | 023104 | [8 empty] | 0 | [21 empty] | 0.0012
Circuit | 133201 | [9 empty] | 4.68 |  |  | 30 | 0.16 | 0.16 | [15 empty] | 0.0009
Circuit | 129902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 59 | 3 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 7.24 | 0.03 | 244.83 | 0.9998 | 0.0286
Circuit | 084201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.28 | 0 | 182.5 | 1 | 0.0055
Circuit | 165901 | [8 empty] | 0
Circuit | 012402 |  |  |  |  | 1 | 1 |  |  | 0 | 10.83 |  |  | 30.02 | 0.36 | 0.89 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0.71 | 0.02 | 42.06 | 1
Circuit | 074802 | [8 empty] | 0
Circuit | 078802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 14 | 0 | 1 | 0 | 0 | 0 | 11 | 1 | 1 | 0 | 0 | 2 | 0.01 | 167.71 | 1 | 0.237
Circuit | 135303 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | 0.02 | 105.3 | 1
Circuit | 079001 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 984 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 983 | 0 | 143.89 | 1.01 | 142.72 | 0.9967 | 0.0799
Circuit | 064103 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 7.57 | 0.12 | 62.24 | 0.9998
Circuit | 155502 | [8 empty] | 0 | 2.13 |  |  | 0 | 1 | 6.12
Circuit | 037602 |  |  |  |  | 1 | 1 | 1 |  | 26 | [6 empty] | 526 | 505 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 1 | 0 | 127.64 | 0.39 | 330.5 | 0.997 | 0.3429
Circuit | 048802 |  |  |  | 1 | 1 | 1 |  |  | 1 | [6 empty] | 46 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 44 | 0 | 12.77 | 0.13 | 101.86 | 0.9997 | 4.6458
Circuit | 151802 | [8 empty] | 0 | [21 empty] | 0.0026
Circuit | 124204 | [8 empty] | 0 | [21 empty] | 0.0037
Circuit | 090804 | [8 empty] | 0
Circuit | 033301 | [8 empty] | 0
Circuit | 097702 |  |  |  |  | 1 | 0.75 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 1.56 | 0 | 387.74 | 1 | 0.004
Circuit | 131201 | [8 empty] | 0 | [6 empty] | 730 | 0 | 0 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0079
Circuit | 122705 |  |  |  |  | 1 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.36 | 0 | 545.15 | 1 | 0.004
Circuit | 068302 | [8 empty] | 0 | [21 empty] | 0.0061
Circuit | 029901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 1 | 0 | 0 | 2.67 | 0.02 | 166.86 | 0.9999 | 0.0767
Circuit | 077202 |  |  |  | 1 | 1 | 0.9 |  |  | 659 | [6 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 4 | 3 | 2.7 | 0.02 | 176.54 | 0.9999 | 0.1865
Circuit | 037002 | [8 empty] | 0
Circuit | 073201 |  |  |  |  | 1 | 1 |  |  | 56 | [6 empty] | 86 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 14.22 | 0.17 | 83.97 | 0.9997 | 0.1713
Circuit | 166402
Circuit | 050202 | [8 empty] | 0
Circuit | 008505 | [8 empty] | 0 | [21 empty] | 0.0084
Circuit | 067601 |  |  |  |  | 1 | 1 |  |  | 0 | 6.21 |  |  | 25.49 | 0.24 | 0.32 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.08 | 0 | 76 | 1
Circuit | 158702 | [8 empty] | 21 | 0 |  |  | 0 | 0 | 0
Circuit | 004602 | [8 empty] | 0 | [21 empty] | 0.0046
Circuit | 044004
Circuit | 031304 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.18 | 0 | 271.6 | 1 | 0.0336
Circuit | 055101 | [8 empty] | 0 | [21 empty] | 0.0015
Circuit | 057601 | [8 empty] | 0 | [21 empty] | 0.0057
Circuit | 064104 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0057
Circuit | 147601 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 362.16 | 1 | 0.0007
Circuit | 006704 | [9 empty] | 0 |  |  | 0 | 0 | 1 | [15 empty] | 0.0215
Circuit | 004603 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 307 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 53 | 0 | 237.99 | 0.72 | 331.78 | 0.9945 | 0.2079
Circuit | 111205 | [8 empty] | 0
Circuit | 107503 |  |  |  | 1 | 1 | 1 |  |  | 0 | 0 |  |  | 5 | 0 | 0 | 642 | 24 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 617 | 30.62 | 0.5 | 61.19 | 0.9993 | 0.0047
Circuit | 048402
Circuit | 061801
Circuit | 127601 |  |  |  |  | 1 | 1 | 1 |  | 0 | 8.54 |  |  | 8.55 | 1 | 0.92 | 45 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.97 | 0.03 | 223.52 | 0.9998 | 0.0139
Circuit | 154601 | [8 empty] | 0
Circuit | 078601 | [30 empty] | 0.2723
Circuit | 086001 | [8 empty] | 0
Circuit | 149702 | [8 empty] | 0
Circuit | 039602 |  |  |  | 0.5 | 1 | 0.993 |  |  | 0 | [6 empty] | 138 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 125 | 0 | 4.8 | 0.04 | 117.49 | 0.9999 | 0.8169
Circuit | 025901 |  |  |  |  | 1 | 1 |  |  | 12 | 0.66 |  |  | 0 | 1 | 1.02 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 3.67 | 0.02 | 217.01 | 0.9999 | 0.0113
Circuit | 018502 |  |  | 1 |  | 1 |  | 1 |  | 1 | 0.65 |  |  | 8.7 | 0.07 | 0.53 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 3.36 | 0.17 | 20.24 | 0.9999 | 2.2339
Circuit | 109301 | [8 empty] | 0 | [6 empty] | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0313
Circuit | 033601 |  |  |  |  | 1 | 1 |  |  | 583 | [6 empty] | 548 | 0 | 0 | 0 | 0 | 0 | 547 | 0 | 0 | 1 | 0 | 59.77 | 0.78 | 76.46 | 0.9986 | 0.2553
Circuit | 091901 | [8 empty] | 0 | [21 empty] | 0.0222
Circuit | 167403 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 45 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.15 | 0.35 | 78.44 | 0.9994 | 0.0538
Circuit | 031803 | [30 empty] | 0.0009
Circuit | 008803 |  |  |  |  | 1 | 1 |  |  | 27 | [6 empty] | 28 | 1 | 0 | 0 | 0 | 1 | 0 | 26 | 0 | 0 | 0 | 4.57 | 0.05 | 101.06 | 0.9999 | 0.1696
Circuit | 034601 | [8 empty] | 0 | [21 empty] | 0.002
Circuit | 067301 | [30 empty] | 0.0278
Circuit | 065401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 226 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 22.76 | 0.23 | 98.07 | 0.9995 | 0.0144
Circuit | 159802 |  |  | 1 |  | 1 | 0 |  |  | 1 | [6 empty] | 19 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11.13 | 0.02 | 542.91 | 0.9997 | 0.9407
Circuit | 085901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 1.3 | 0.02 | 74.81 | 1 | 0.0068
Circuit | 166401 | [8 empty] | 0
Circuit | 022202 |  |  |  |  | 1 |  | 1 |  | 173 | 0 |  |  | 3 | 0 | 0 | 1280 | 0 | 166 | 0 | 0 | 0 | 4 | 1110 | 0 | 0 | 0 | 153.72 | 0.98 | 157.32 | 0.9964 | 0.1656
Circuit | 035801 |  |  |  | 1 | 1 | 0.836 |  |  | 132 | [6 empty] | 159 | 37 | 0 | 0 | 0 | 1 | 1 | 26 | 0 | 28 | 66 | 179.97 | 0.7 | 255.8 | 0.9958 | 2.9027
Circuit | 098203 | [8 empty] | 0
Circuit | 134701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0.01 | 269.71 | 0.9999
Circuit | 002001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.31 | 0 | 160 | 1 | 1.0212
Circuit | 037301 |  |  |  |  | 1 | 0.957 |  |  | 0 | [6 empty] | 23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 4.01 | 0.03 | 127.4 | 0.9999 | 0.011
Circuit | 079302 |  |  | 1 |  | 1 | 1 | 1 |  | 4 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.07 | 0 | 51.5 | 1
Circuit | 035103 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 129 | 0 | 122 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 10.06 | 0.08 | 128.01 | 0.9998 | 0.9086
Circuit | 147201 |  |  | 0.5 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1385 | 1328 | 0 | 0 | 0 | 0 | 18 | 3 | 0 | 36 | 0 | 241.57 | 1.04 | 231.63 | 0.9944 | 0.7568
Circuit | 076702 | [8 empty] | 0 | [21 empty] | 0.0023
Circuit | 060801 |  |  |  |  | 1 | 1 |  |  | 0 | 0.64 |  |  | 1.12 | 0.57 | 0.57 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 2.28 | 0.03 | 89.88 | 0.9999 | 0.0032
Circuit | 067701 | [8 empty] | 0 | [21 empty] | 0.0169
Circuit | 056803 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 17 | 2.55 | 0.05 | 52.26 | 0.9999 | 0.0016
Circuit | 010106 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.16 | 0 | 288 | 1 | 0.0205
Circuit | 020502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.41 | 0 | 340.19 | 1 | 0.1144
Circuit | 151901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54 | 0 | 395.02 | 1 | 0.0165
Circuit | 006202 |  |  |  |  | 1 | 1 |  |  | 0 | 5.48 |  |  | 0 | 1 | 1.59 | 35 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 2.24 | 0.03 | 84.25 | 0.9999 | 0.0008
Circuit | 095304 | [30 empty] | 0.0079
Circuit | 069901 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 138 | 0 | 0 | 0 | 0 | 0 | 1 | 136 | 1 | 0 | 0 | 12.04 | 0.06 | 212.53 | 0.9997 | 0.0193
Circuit | 107604 | [8 empty] | 0 | [21 empty] | 0.0049
Circuit | 075901 |  |  | 1 |  | 1 | 1 |  |  | 191 | [6 empty] | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.39 | 0 | 167.23 | 1 | 0.3485
Circuit | 042703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0 | 388 | 1
Circuit | 137303 | [8 empty] | 0
Circuit | 049202 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.55 | 0 | 257.12 | 1 | 0.0021
Circuit | 031701 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0.55 | 0.01 | 59.87 | 1 | 0.0526
Circuit | 152703 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.31 | 0.04 | 119.63 | 0.9999 | 0.014
Circuit | 053702 | [30 empty] | 0.0029
Circuit | 074602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.23 | 0 | 65.06 | 1 | 0.0036
Circuit | 112604 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0.02 | 76.85 | 1
Circuit | 156402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.05 | 0 | 91.18 | 1
Circuit | 079702 |  |  |  |  | 1 | 1 |  |  | 0 | 0.13 |  |  | 0 | 1 | 1.14 | 18 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 2.4 | 0.02 | 150.66 | 0.9999 | 0.0868
Circuit | 022701 |  |  | 1 | [5 empty] | 0 | [21 empty] | 0.0198
Circuit | 072401 |  |  | 1 |  | 1 | 1 |  |  | 0 | 4.41 |  |  | 4.96 | 0.89 | 1.01 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.15 | 0 | 175.6 | 1 | 0.006
Circuit | 162001 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.5 | 0 | 143.91 | 1 | 0.0158
Circuit | 076202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.14 | 0 | 112.97 | 1 | 0.0012
Circuit | 024902 |  |  | 1 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 543 | 1 | 0 | 0 | 0 | 0 | 460 | 82 | 0 | 0 | 0 | 188.31 | 0.94 | 200.79 | 0.9956 | 0.6736
Circuit | 117902 | [8 empty] | 0 | [21 empty] | 0.001
Circuit | 061301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 187 | 149 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 25.1 | 0.16 | 155.86 | 0.9994 | 0.093
Circuit | 021903 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 0.04 | 40.71 | 1 | 0.0049
Circuit | 026004 | [8 empty] | 0 | [21 empty] | 0.0038
Circuit | 071203 |  |  |  |  | 1 | 1 |  |  | 5 | [6 empty] | 41 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.15 | 0.02 | 92.54 | 1 | 0.0062
Circuit | 159702 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 91 | 5 | 0 | 0 | 0 | 0 | 84 | 1 | 1 | 0 | 0 | 4.83 | 0.07 | 65.03 | 0.9999 | 0.4641
Circuit | 003703 | [30 empty] | 0.0043
Circuit | 058903 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 661 | 152 | 0 | 509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.24 | 0.3 | 174.58 | 0.9988 | 0.0098
Circuit | 072704 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.68 | 0.02 | 116.84 | 0.9999 | 0.0034
Circuit | 056801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 3 | 0.01 | 333.8 | 0.9999 | 0.0188
Circuit | 022802 | [8 empty] | 0 | [21 empty] | 0.0069
Circuit | 121001 | [8 empty] | 0
Circuit | 104102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.21 | 0 | 69.48 | 1 | 0.0237
Circuit | 117903 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.23 | 0 | 304 | 1 | 0.003
Circuit | 108803 | [8 empty] | 0
Circuit | 033501 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 7.15 | 0.06 | 128.15 | 0.9998 | 1.1788
Circuit | 063001 |  |  |  |  | 1 | 0.982 |  |  | 6 | [6 empty] | 55 | 52 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 17.54 | 0.16 | 108.09 | 0.9996 | 0.9292
Circuit | 048502 |  |  |  |  | 1 | 0.87 |  |  | 1 | 0.44 |  |  | 0 | 1 | 0.93 | 25 | 2 | 0 | 2 | 0 | 0 | 2 | 2 | 1 | 16 | 0 | 5.04 | 0.03 | 194.89 | 0.9999 | 0.8056
Circuit | 058002 |  |  |  |  | 1 | 1 | [9 empty] | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 48 | 1 | 0.0046
Circuit | 072103 | [8 empty] | 0
Circuit | 104202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 122 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.05 | 0.12 | 104.13 | 0.9997
Circuit | 069802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0.47 | 0 | 151.67 | 1
Circuit | 040701 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3.46 | 0 | 1104 | 0.9999 | 0.1411
Circuit | 122601 | [8 empty] | 0 | [21 empty] | 0.0005
Circuit | 051801 |  |  |  | 1 | 1 | 0.998 |  |  | 0 | 12.81 |  |  | 19.35 | 0.66 | 0.79 | 448 | 13 | 0 | 41 | 0 | 0 | 255 | 102 | 0 | 37 | 0 | 72.23 | 0.39 | 184.03 | 0.9983 | 0.3558
Circuit | 108203 | [8 empty] | 0 | [21 empty] | 0.964
Circuit | 069902 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 10 | 0 | 1 | 0 | 0 | 6 | 0 | 0 | 0.19 | 0 | 83.53 | 1
Circuit | 162802 | [8 empty] | 0 | [21 empty] | 0.0134
Circuit | 036903
Circuit | 037403 | [30 empty] | 0.0017
Circuit | 093402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0.33 | 0.01 | 55.35 | 1 | 0.0022
Circuit | 002401 | [8 empty] | 0
Circuit | 034003 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 115 | 1
Circuit | 072802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 35 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 3.31 | 0.03 | 127.11 | 0.9999 | 0.0275
Circuit | 102502 | [8 empty] | 2 | [21 empty] | 0.0023
Circuit | 093202 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0 | 136 | 1 | 0.0204
Circuit | 157402 | [8 empty] | 0
Circuit | 082904 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 14 | 0 | 1.26 | 0.02 | 83.01 | 1 | 0.0027
Circuit | 041602 | [8 empty] | 0
Circuit | 013502 | [8 empty] | 0 | [21 empty] | 0.0026
Circuit | 106102 | [8 empty] | 0
Circuit | 010401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 2.48 | 0.03 | 75.68 | 0.9999 | 0.3233
Circuit | 037902 |  |  |  |  | 1 | 1 |  |  | 103 | [6 empty] | 1742 | 622 | 0 | 0 | 0 | 0 | 1119 | 1 | 0 | 0 | 0 | 73.34 | 1.63 | 45.01 | 0.9983 | 1.0309
Circuit | 074402 | [30 empty] | 0.0102
Circuit | 009901 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 0 | 581.72 | 1 | 1.9552
Circuit | 041202 |  |  | 1 |  | 1 |  | 1 |  | 333 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.27 | 0 | 207.85 | 1 | 0.5843
Circuit | 000402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 524 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 203 | 0 | 30.46 | 0.53 | 57.44 | 0.9993 | 0.0243
Circuit | 001401 | [8 empty] | 1
Circuit | 081801 | [8 empty] | 0 | [21 empty] | 0.0385
Circuit | 033103 | [8 empty] | 0 | 0.77 |  |  | 1.06 | 0.72 | 0.72 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0012
Circuit | 034503 | [8 empty] | 0
Circuit | 159801 |  |  |  |  | 1 | 0.431 |  |  | 127 | [6 empty] | 397 | 0 | 0 | 0 | 0 | 0 | 360 | 36 | 0 | 1 | 0 | 165.42 | 0.41 | 407.1 | 0.9962 | 1.2068
Circuit | 127403 |  |  |  |  | 1 | 0.222 | 1 |  | 62 | 13.92 |  |  | 26.35 | 0.53 | 0.74 | 46 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 37 | 0 | 24.49 | 0.13 | 195.95 | 0.9994 | 0.3125
Circuit | 061102 |  |  | 1 |  | 1 | 0.675 |  |  | 1 | [6 empty] | 336 | 335 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.49 | 0.14 | 317.83 | 0.999 | 1.7431
Circuit | 034702 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 117 | 43 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 51 | 22.67 | 0.11 | 208.64 | 0.9995 | 1.0687
Circuit | 066902
Circuit | 168601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 96 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 6.32 | 0.05 | 137.61 | 0.9999 | 0.0024
Circuit | 005802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 68 | 1
Circuit | 115902 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0095
Circuit | 054901 | [8 empty] | 0
Circuit | 127302 |  |  |  |  | 1 | 0.964 |  |  | 0 | [6 empty] | 28 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 23 | 0.98 | 0.01 | 84.16 | 1 | 0.0142
Circuit | 137201 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 237 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 236 | 0 | 0 | 30.08 | 0.29 | 102.04 | 0.9993 | 0.0174
Circuit | 129601 | [8 empty] | 0 | [21 empty] | 0.0018
Circuit | 158901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0 | 170.85 | 1 | 0.0094
Circuit | 025104 | [8 empty] | 0 | [21 empty] | 0.005
Circuit | 026003 | [8 empty] | 0 | [21 empty] | 0.0029
Circuit | 067201 | [8 empty] | 0 | [21 empty] | 0.8197
Circuit | 031303 | [8 empty] | 0 | [21 empty] | 0.0019
Circuit | 051902
Circuit | 051201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 96 | 93 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 9.99 | 0.09 | 115.67 | 0.9998 | 0.1592
Circuit | 156301 | [8 empty] | 0
Circuit | 109202 | [9 empty] | 0 |  |  | 1.57 | 0 | 0
Circuit | 108804 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 31.72 | 0.16 | 200.25 | 0.9993 | 0.0099
Circuit | 099101 | [8 empty] | 0 | [21 empty] | 0.8429
Circuit | 085802 |  |  |  |  | 1 | 1 | 1 |  | 12 | [6 empty] | 50 | 12 | 26 | 0 | 0 | 0 | 0 | 1 | 0 | 11 | 0 | 15.18 | 0.13 | 119.89 | 0.9996 | 0.0076
Circuit | 061502 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0 | 55 | 1 | 0.0014
Circuit | 071101 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 112 | 0 | 0 | 0 | 0 | 0 | 104 | 8 | 0 | 0 | 0 | 9.02 | 0.09 | 96.09 | 0.9998 | 0.0411
Circuit | 075902 |  |  |  |  | 1 | 1 |  |  | 43 | 0 |  |  | 2 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.48 | 0.01 | 158.98 | 1 | 0.0053
Circuit | 111803 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 13.99 | 0.04 | 374.29 | 0.9997 | 0.8785
Circuit | 057303 |  |  |  |  | 1 | 1 |  |  | 1 | 0 |  |  | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1 | 0 | 0 | 0.48 | 0 | 98.7 | 1 | 0.0059
Circuit | 077402 |  |  |  |  | 1 | 1 | 1 |  | 15 | [6 empty] | 5033 | 0 | 0 | 0 | 0 | 0 | 0 | 3805 | 0 | 1228 | 0 | 114.8 | 1.33 | 86.61 | 0.9973 | 0.005
Circuit | 140701 |  |  |  |  | 1 | 0.995 | 1 |  | 0 | [6 empty] | 214 | 205 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 18.44 | 0.17 | 109.67 | 0.9996 | 1.2168
Circuit | 062301 | [30 empty] | 0.0025
Circuit | 009004 | [8 empty] | 0 | [21 empty] | 0.0046
Circuit | 162801 |  |  |  |  | 1 | 1 |  |  | 6 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 6.3 | 0.01 | 435.27 | 0.9999 | 0.0495
Circuit | 048203 |  |  |  | 1 | 1 | 1 |  |  | 0 | 0 |  |  | 1.21 | 0 | 1 | 28 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0.09 | 0.01 | 6.86 | 1
Circuit | 024105 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.9788
Circuit | 041002 | [8 empty] | 0 | [21 empty] | 0.6472
Circuit | 100203 | [30 empty] | 0.0008
Circuit | 070002 |  |  | 1 | [5 empty] | 0 | [21 empty] | 0.0095
Circuit | 123301 | [8 empty] | 0 | [21 empty] | 0.9858
Circuit | 157702 | [8 empty] | 0
Circuit | 021601 | [8 empty] | 0 | [21 empty] | 0.0019
Circuit | 024402 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0.43 | 0 | 128.81 | 1 | 0.0081
Circuit | 075704 | [30 empty] | 0.0019
Circuit | 070902 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 154 | 0 | 1 | 0 | 0 | 0 | 22 | 131 | 0 | 0 | 0 | 69.05 | 0.31 | 221.94 | 0.9984 | 0.1838
Circuit | 097301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 0 | 268 | 1 | 0.0013
Circuit | 000601 |  |  |  |  | 1 | 1 |  |  | 0 | 20.36 |  |  | 41.9 | 0.49 | 0.56 | 177 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 164 | 0 | 9.02 | 0.18 | 50.37 | 0.9998 | 0.0425
Circuit | 064703 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.41 | 0 | 1333.06 | 1 | 0.566
Circuit | 031802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.69 | 0 | 325.32 | 1
Circuit | 091801 |  |  | 1 |  | 1 | 1 | 1 |  | 43 | [6 empty] | 216 | 0 | 0 | 0 | 0 | 1 | 215 | 0 | 0 | 0 | 0 | 65.57 | 0.28 | 231.03 | 0.9985 | 1.2694
Circuit | 024503 | [8 empty] | 0 | [21 empty] | 0.008
Circuit | 111301 | [8 empty] | 0
Circuit | 071001 | [8 empty] | 464 | [21 empty] | 0.0023
Circuit | 067504 | [8 empty] | 0 | [21 empty] | 0.0009
Circuit | 061903
Circuit | 059501 | [8 empty] | 1 | 0 |  |  | 0 | 0 | 1 | [15 empty] | 0.1503
Circuit | 118403 | [8 empty] | 0
Circuit | 030701 | [8 empty] | 0 | [21 empty] | 0.9918
Circuit | 032701 | [8 empty] | 87 | 4.71 |  |  | 4.67 | 1.01 | 1 | [15 empty] | 0.005
Circuit | 029404 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 48 | 47 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.73 | 0.03 | 99.43 | 0.9999 | 0.0006
Circuit | 104401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 152.6 | 1 | 0.008
Circuit | 041301
Circuit | 043601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.48 | 0 | 184 | 1 | 0.739
Circuit | 005602 |  |  | 1 |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 44 | 0 | 0 | 7 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 6.36 | 0.04 | 152.89 | 0.9999 | 0.0304
Circuit | 051903 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 83 | 0 | 0 | 0 | 0 | 5 | 71 | 0 | 0 | 0 | 7 | 5.3 | 0.05 | 103.44 | 0.9999 | 0.2551
Circuit | 140702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.68 | 0 | 260.5 | 1 | 2.5217
Circuit | 125203 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0.75 | 0 | 183.61 | 1 | 0.0057
Circuit | 020101 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 58 | 2 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 27.44 | 0.06 | 425.39 | 0.9994 | 0.1746
Circuit | 113401 | [9 empty] | 3.79 |  |  | 0 | 1 | 1
Circuit | 140401 |  |  |  | 1 | 1 | 0.6 |  |  | 0 | [6 empty] | 5 | 2 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.51 | 0 | 410.71 | 1 | 1.0841
Circuit | 155001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 31 | 0 | 23 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 0 | 7.9 | 0.07 | 106.07 | 0.9998 | 0.5913
Circuit | 108801
Circuit | 085702 |  |  |  |  | 1 | 1 |  |  | 2 | 0 |  |  | 15.89 | 0 | 0.2 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 1 | 2.52 | 0.47 | 5.3 | 0.9999 | 0.0102
Circuit | 061101
Circuit | 132202 | [8 empty] | 0 | [21 empty] | 0.3436
Circuit | 078401 | [8 empty] | 0 | [21 empty] | 0.031
Circuit | 150901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.76 | 0.01 | 78 | 1 | 0.2941
Circuit | 129901 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.37 | 0.03 | 247.42 | 0.9999 | 0.0515
Circuit | 068604 |  |  | 1 | [5 empty] | 0 | [21 empty] | 0.0087
Circuit | 057502 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 32 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 7.01 | 0.03 | 210.16 | 0.9998 | 0.0542
Circuit | 159202 | [8 empty] | 0
Circuit | 051202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0.2 | 0.02 | 11.13 | 1 | 0.0063
Circuit | 021301 | [8 empty] | 0 | [21 empty] | 0.0044
Circuit | 045103 | [8 empty] | 0 | [21 empty] | 0.9793
Circuit | 114203 | [8 empty] | 0 | [21 empty] | 0.0014
Circuit | 106504 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0.15 | 0.03 | 5.34 | 1 | 0.0086
Circuit | 135302 | [8 empty] | 1 | [21 empty] | 0.0014
Circuit | 066502 | [8 empty] | 0 | [21 empty] | 0.0025
Circuit | 042002 |  |  |  |  | 1 | 1 |  |  | 52 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.04 | 0 | 44 | 1 | 0.0019
Circuit | 127901 | [8 empty] | 0 | [21 empty] | 0.0156
Circuit | 169304 |  |  |  | 1
Circuit | 041303 | [8 empty] | 0
Circuit | 010402 | [8 empty] | 0 | [21 empty] | 0.0053
Circuit | 014301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0.34 | 0 | 85.43 | 1 | 0.004
Circuit | 141201 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 3 | 0 | 0.87 | 125 | 11 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 53 | 1.53 | 0.02 | 68.96 | 1 | 0.2726
Circuit | 054201 |  |  |  |  | 1 | 0.057 |  |  | 0 | [6 empty] | 866 | 849 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 9 | 0 | 1258.9 | 1.07 | 1177.5 | 0.9709 | 0.1494
Circuit | 071002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 215 | 0 | 0 | 1 | 0 | 0 | 152 | 0 | 0 | 0 | 62 | 24.68 | 0.26 | 95.15 | 0.9994 | 0.8327
Circuit | 076903
Circuit | 168602 | [8 empty] | 1 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0058
Circuit | 155802 |  |  |  |  | 1 | 1 |  |  | 21 | [6 empty] | 36 | 9 | 0 | 0 | 0 | 0 | 15 | 0 | 1 | 11 | 0 | 10.12 | 0.06 | 178.87 | 0.9998 | 0.2563
Circuit | 020902 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Circuit | 048602 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 63 | 2 | 0 | 0 | 0 | 0 | 54 | 7 | 0 | 0 | 0 | 11.29 | 0.05 | 238.08 | 0.9997 | 1.0655
Circuit | 049901 |  |  |  |  | 1 | 1 |  |  | 0 | 1.53 |  |  | 2.1 | 0.73 | 0.99 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 365 | 1
Circuit | 017902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.12 | 0 | 130.94 | 1 | 0.0047
Circuit | 077102 | [8 empty] | 0 | [21 empty] | 0.0032
Circuit | 048801 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 105 | 0 | 101 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 21.12 | 0.14 | 151.87 | 0.9995 | 0.0026
Circuit | 149502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 141 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 32.51 | 0.52 | 62.03 | 0.9992 | 0.6989
Circuit | 021403 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 2.45 | 0 | 0 | 367 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.67 | 1 | 8.67 | 0.9998 | 0.0409
Circuit | 068301 | [8 empty] | 0 | [21 empty] | 0.013
Circuit | 025103 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.27 | 0 | 261.55 | 1 | 0.001
Circuit | 028002 | [8 empty] | 0 | [21 empty] | 0.0019
Circuit | 137102 | [8 empty] | 0
Circuit | 036303 | [8 empty] | 0 | [6 empty] | 893 | 0 | 0 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1.0202
Circuit | 090803 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.04 | 0 | 27 | 1 | 0.0064
Circuit | 021703 |  |  | 1 |  | 1 | 0 |  |  | 0 | [6 empty] | 1771 | 1761 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 525.05 | 1.01 | 518.23 | 0.9878 | 1.3352
Circuit | 015501 | [8 empty] | 0 | 2.48 |  |  | 2.57 | 0.96 | 1
Circuit | 058101 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.27 | 0 | 93.42 | 1 | 0.0071
Circuit | 086004 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 150 | 1 | 0.0034
Circuit | 122701 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161.87 | 0.31 | 518 | 0.9963 | 0.0938
Circuit | 169302
Circuit | 017901 | [8 empty] | 0
Circuit | 166303 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 63 | 0 | 0 | 0 | 0 | 0 | 50 | 2 | 0 | 11 | 0 | 18.45 | 0.17 | 110.39 | 0.9996
Circuit | 061401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.25 | 0 | 88.5 | 1 | 0.0014
Circuit | 004601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66 | 0 | 262.18 | 1 | 0.0008
Circuit | 006706 | [30 empty] | 0.0039
Circuit | 149701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.53 | 0.01 | 106.12 | 1
Circuit | 063602 |  |  |  |  | 1 | 0.999 |  |  | 0 | [6 empty] | 1130 | 0 | 0 | 115 | 0 | 0 | 1014 | 1 | 0 | 0 | 0 | 72.34 | 1.07 | 67.85 | 0.9983 | 1.9485
Circuit | 029502 | [8 empty] | 0
Circuit | 033803 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 43 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 1 | 2.55 | 0.03 | 98.74 | 0.9999 | 0.0018
Circuit | 129001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 62 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 2 | 0 | 0 | 17.31 | 0.09 | 195.42 | 0.9996 | 0.2871
Circuit | 162602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0.74 | 0.01 | 90.74 | 1 | 0.0073
Circuit | 084202 | [30 empty] | 0.003
Circuit | 153002 | [8 empty] | 0
Circuit | 060901 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0 | 495 | 1 | 0.0032
Circuit | 116502 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 42 | 0 | 27 | 0 | 0 | 0 | 1 | 14 | 0 | 0 | 0 | 41.07 | 0.25 | 167.23 | 0.999 | 0.0117
Circuit | 045301 |  |  | 1 |  | 1 | 1 | 1 |  | 7 | [6 empty] | 1187 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 1 | 216.8 | 1.74 | 124.93 | 0.995 | 0.7222
Circuit | 007103 | [8 empty] | 0 | [21 empty] | 0.0019
Circuit | 127702 |  |  |  |  | 1 | 0.875 |  |  | 0 | [6 empty] | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.01 | 380.5 | 0.9999 | 1.4173
Circuit | 115501 | [8 empty] | 0 | [6 empty] | 279 | 0 | 0 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Circuit | 042901 |  |  |  |  | 1 | 1 |  |  | 1 | 0 |  |  | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1.58 | 0.01 | 307.46 | 1 | 0.1491
Circuit | 032102 | [8 empty] | 0 | [21 empty] | 0.988
Circuit | 029702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.09 | 0 | 174 | 1 | 0.0016
Circuit | 064802 | [30 empty] | 0.0006
Circuit | 005401 |  |  |  |  | 1 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0 | 625 | 1 | 0.0218
Circuit | 039504 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.04 | 0 | 67 | 1 | 0.0043
Circuit | 075702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 59 | 0 | 0 | 28 | 0 | 0 | 9 | 0 | 22 | 0 | 0 | 0.99 | 0.01 | 68.97 | 1 | 0.0406
Circuit | 061302 |  |  |  |  | 1 | 0 | 1 | [8 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1.59 | 0 | 396.75 | 1 | 0.002
Circuit | 117905 | [8 empty] | 0
Circuit | 032302 |  |  |  |  | 1 | 0.6 |  |  | 1 | [6 empty] | 5 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | 0.01 | 407.85 | 1 | 0.0959
Circuit | 017005
Circuit | 100901 |  |  |  |  | 1 | 0.5 |  |  | 0 | 0.65 |  |  | 0.38 | 1.69 | 1.28 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.78 | 0 | 570.5 | 1 | 0.0157
Circuit | 002502 | [30 empty] | 0.0023
Circuit | 041901 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.14 | 0 | 120.32 | 1 | 0.0196
Circuit | 030702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 4 | 0 | 3.57 | 0.04 | 90.38 | 0.9999 | 0.9898
Circuit | 112002
Circuit | 130902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.81 | 0.03 | 209 | 0.9999 | 0.0278
Circuit | 115901 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 3 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 173.76 | 1 | 5.1292
Circuit | 125101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 56 | 16 | 38 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7.97 | 0.06 | 134.84 | 0.9998 | 1.1742
Circuit | 130906 | [8 empty] | 0 | [21 empty] | 0.0135
Circuit | 158902 | [30 empty] | 0.0103
Circuit | 091501 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 88 | 0 | 0 | 77 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0.96 | 0.01 | 82.08 | 1 | 0.1325
Circuit | 035802 | [8 empty] | 0 | [21 empty] | 0.3493
Circuit | 024701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.16 | 0 | 110.29 | 1
Circuit | 039501
Circuit | 004102 | [8 empty] | 0 | [21 empty] | 0.006
Circuit | 054802 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.05 | 0 | 100.51 | 1 | 0.0114
Circuit | 064201 | [8 empty] | 22 | [21 empty] | 0.0015
Circuit | 040503 | [8 empty] | 1 | [21 empty] | 0.0043
Circuit | 148202 | [8 empty] | 0 | [21 empty] | 0.0021
Circuit | 036403 | [8 empty] | 0 | [21 empty] | 0.0053
Circuit | 040401 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.47 | 0.01 | 251.7 | 1 | 0.0078
Circuit | 050101 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.02 | 0.03 | 70.98 | 1 | 0.0199
Circuit | 010916
Circuit | 113404 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 78.19 | 1.02 | 76.77 | 0.9982 | 0.0736
Circuit | 070304 | [8 empty] | 2 | [21 empty] | 0.01
Circuit | 106902 |  |  |  |  | 1 | 0.75 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 3.46 | 0.01 | 392.62 | 0.9999
Circuit | 040301
Circuit | 112601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 14 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 0 | 0 | 3 | 0.69 | 0.01 | 47.27 | 1
Circuit | 151402 |  |  |  |  | 1 | 0.75 | 1 |  | 0 | [6 empty] | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.09 | 0.03 | 306.56 | 0.9998 | 0.0014
Circuit | 154502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.15 | 0 | 44.78 | 1
Circuit | 150602 | [9 empty] | 0 |  |  | 5.67 | 0 | 0
Circuit | 115004 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 0 | 369.94 | 1 | 0.0117
Circuit | 063404 | [8 empty] | 1 | 0 |  |  | 6 | 0 | 0 | [15 empty] | 0.0153
Circuit | 163702 | [8 empty] | 0
Circuit | 104801 | [8 empty] | 0 | [21 empty] | 0.219
Circuit | 002402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0.79 | 0.01 | 81.31 | 1 | 0.0057
Circuit | 106501 | [8 empty] | 0 | [21 empty] | 0.0086
Circuit | 131402 |  |  |  |  | 1 |  | 1 |  | 0 | 0 |  |  | 0.01 | 0 | 0.82 | 18 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 5.13 | 0.05 | 105.64 | 0.9999 | 1.1617
Circuit | 006402 | [8 empty] | 1 | [21 empty] | 0.004
Circuit | 051802 | [30 empty] | 0.457
Circuit | 054601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.38 | 0 | 407.4 | 1
Circuit | 040303 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 0 | 1186 | 1 | 0.0029
Circuit | 017301 | [8 empty] | 0 | [21 empty] | 0.012
Circuit | 124205 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 4.33 | 0 | 913.77 | 0.9999 | 0.0008
Circuit | 048301 |  |  |  | 1 | 1 | 0.993 | 1 |  | 108 | 11.52 |  |  | 34.95 | 0.33 | 0.49 | 504 | 2 | 361 | 0 | 0 | 1 | 1 | 0 | 2 | 137 | 0 | 32.36 | 0.21 | 153.19 | 0.9993 | 0.7728
Circuit | 093902 |  |  |  | 1 | 1 | 0.775 |  |  | 0 | 4.18 |  |  | 1.29 | 3.24 | 1.18 | 142 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 21.13 | 0.08 | 271.9 | 0.9995 | 0.7072
Circuit | 157201 | [8 empty] | 0
Circuit | 085803 |  |  |  |  | 1 | 1 |  |  | 0 | 5.97 |  |  | 0 | 1 | 2.6 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 1.23 | 0.02 | 67.62 | 1 | 0.0049
Circuit | 026502 | [8 empty] | 80 | [6 empty] | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0022
Circuit | 093503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 338 | 1
Circuit | 106601 |  |  |  |  | 1 | 0.031 |  |  | 0 | [6 empty] | 92 | 1 | 0 | 28 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 36 | 0.06 | 559.07 | 0.9992 | 0.0493
Circuit | 093901 | [8 empty] | 0 | [21 empty] | 0.0032
Circuit | 038301 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.08 | 0 | 80.98 | 1 | 0.001
Circuit | 152801 | [8 empty] | 0
Circuit | 150701 | [8 empty] | 0 | [21 empty] | 0.0029
Circuit | 032702 | [8 empty] | 3 | [21 empty] | 0.0018
Circuit | 039701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 1 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1.5 | 0.01 | 209.97 | 1 | 0.3256
Circuit | 034103
Circuit | 140703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 160 | 1 | 1.0235
Circuit | 053701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.27 | 0 | 234.68 | 1 | 0.0006
Circuit | 102901
Circuit | 159701 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 119 | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | 46.4 | 0.19 | 240.57 | 0.9989 | 0.0097
Circuit | 112201 |  |  |  |  | 1 | 0.991 | 1 |  | 1 | [6 empty] | 117 | 1 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 24 | 0 | 2.92 | 0.08 | 35.27 | 0.9999 | 0.0474
Circuit | 103801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0.01 | 67 | 1
Circuit | 112802 |  |  |  |  | 1 | 1 |  |  | 154 | [6 empty] | 309 | 0 | 0 | 0 | 0 | 0 | 154 | 154 | 0 | 1 | 0 | 47.77 | 0.31 | 151.96 | 0.9989 | 0.0122
Circuit | 093802 |  |  |  |  | 1 | 1 |  |  | 1780 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 215.72 | 1 | 0.0033
Circuit | 150601 | [9 empty] | 0 |  |  | 8.5 | 0 | 0 | [15 empty] | 0.0011
Circuit | 125603 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0 | 379 | 1
Circuit | 071102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 21 | 0 | 1.65 | 0.03 | 63.85 | 1 | 0.0021
Circuit | 028901 |  |  | 1 | [5 empty] | 0 | [21 empty] | 0.0916
Circuit | 114602 | [8 empty] | 0 | [21 empty] | 0.0028
Circuit | 026401 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.12 | 0 | 259.05 | 1 | 0.0052
Circuit | 147602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 133.78 | 1
Circuit | 033101 | [8 empty] | 0 | [21 empty] | 0.0005
Circuit | 008504 | [8 empty] | 0
Circuit | 137802 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.01 | 90.85 | 1 | 0.5231
Circuit | 124502 | [8 empty] | 0 | [21 empty] | 0.001
Circuit | 167901 |  |  |  |  | 1 | 1 |  |  | 110 | [6 empty] | 707 | 707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325.04 | 1.27 | 255.61 | 0.9925 | 0.2212
Circuit | 144201 | [8 empty] | 0 | [21 empty] | 0.038
Circuit | 029603 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 37 | 0 | 0 | 15 | 0 | 1 | 6 | 0 | 0 | 15 | 0 | 3.33 | 0.02 | 167.63 | 0.9999 | 0.0678
Circuit | 079602 | [30 empty] | 0.0075
Circuit | 042701 | [8 empty] | 1 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Circuit | 002302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 24 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.05 | 0 | 101 | 1 | 0.0027
Circuit | 135201 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 32 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 30 | 0 | 11.5 | 0.05 | 231.53 | 0.9997 | 0.0016
Circuit | 025301 |  |  | 0 |  | 1 | 1 | 1 |  | 0 | [6 empty] | 23 | 13 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 4.8 | 0.02 | 253.13 | 0.9999 | 0.2251
Circuit | 118402 | [8 empty] | 0 | [21 empty] | 0.3475
Circuit | 008502 | [8 empty] | 1 | [21 empty] | 0.0194
Circuit | 052602 |  |  |  |  | 1 | 1 |  |  | 0 | 3.3 |  |  | 4.23 | 0.78 | 0.98 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.03 | 0 | 40 | 1 | 0.0107
Circuit | 042702 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.21 | 0 | 113.52 | 1 | 0.0166
Circuit | 029802 |  |  |  |  | 1 | 1 | 1 |  | 145 | [6 empty] | 57 | 15 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 1 | 0 | 8.82 | 0.12 | 76.29 | 0.9998 | 3.643
Circuit | 011004 | [8 empty] | 0 | [21 empty] | 0.0031
Circuit | 101203 | [8 empty] | 0
Circuit | 002801 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 427 | 0 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1.75 | 0 | 369.5 | 1 | 0.0071
Circuit | 090702 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 1 | 0 | 0 | 2 | 0.02 | 98.56 | 1 | 0.0157
Circuit | 049903 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.06 | 0 | 476.94 | 1 | 0.0122
Circuit | 029002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 94 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.74 | 0.08 | 141.47 | 0.9997 | 0.2763
Circuit | 068603 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1987 | 0 | 33 | 0 | 0 | 0 | 0 | 1954 | 0 | 0 | 0 | 174.7 | 1.02 | 171.01 | 0.996 | 0.3568
Circuit | 122704 | [30 empty] | 0.0054
Circuit | 036302 | [30 empty] | 1.0517
Circuit | 024202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.32 | 0 | 188.8 | 1 | 0.0486
Circuit | 024501 |  |  | 1 |  | 1 | 1 | 1 |  | 0 | 0 |  |  | 0 | 0 | 1 | 20 | 16 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 6.6 | 0.02 | 379.7 | 0.9998 | 0.013
Circuit | 133501 |  |  |  |  | 1 | 1 |  |  | 25 | [6 empty] | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 28 | 0 | 2.13 | 0.02 | 103.54 | 1 | 0.0014
Circuit | 036101
Circuit | 064202 | [8 empty] | 0 | [21 empty] | 0.3513
Circuit | 078001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 2.28 | 0.01 | 223.04 | 0.9999 | 0.017
Circuit | 151902 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.38 | 0 | 852 | 1
Circuit | 043304 | [30 empty] | 0.0038
Circuit | 103702 | [8 empty] | 0
Circuit | 050903 |  |  |  |  | 1 | 0.126 |  |  | 1769 | [6 empty] | 1883 | 0 | 0 | 1772 | 0 | 0 | 98 | 0 | 0 | 0 | 13 | 39.92 | 0.06 | 637.3 | 0.9991 | 0.0615
Circuit | 057702 | [30 empty] | 0.9985
Circuit | 019602 |  |  |  |  | 1 | 1 |  |  | 89 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.05 | 0 | 54 | 1 | 0.0036
Circuit | 054301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 77 | 76 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8.03 | 0.04 | 191.67 | 0.9998
Circuit | 037702 |  |  |  |  | 1 | 1 | 1 |  | 209 | 0 |  |  | 0 | 0 | 1 | 298 | 0 | 0 | 1 | 0 | 0 | 0 | 140 | 0 | 0 | 157 | 29.9 | 0.24 | 126.03 | 0.9993 | 1.3778
Circuit | 091703 | [8 empty] | 0
Circuit | 149302 | [8 empty] | 0 | [21 empty] | 0.0022
Circuit | 021702 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 1387 | 1387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.49 | 1 | 412 | 0.9904 | 1.0065
Circuit | 036001 |  |  |  |  | 1 | 1 |  |  | 0 | 0.45 |  |  | 0 | 314.17 | 1.07 | 60 | 1 | 0 | 48 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 1.39 | 0.02 | 79.7 | 1 | 0.0102
Circuit | 147801 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1.9255
Circuit | 014502 |  |  |  |  | 1 | 1 | 1 |  | 87 | 3.59 |  |  | 15.44 | 0.23 | 0.54 | 182 | 0 | 0 | 0 | 0 | 0 | 86 | 3 | 0 | 93 | 0 | 15.12 | 0.12 | 128.97 | 0.9996 | 0.0006
Circuit | 081601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 74.95 | 1 | 0.0012
Circuit | 060804 | [8 empty] | 0 | [21 empty] | 0.0129
Circuit | 002904 | [30 empty] | 0.0313
Circuit | 031902 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.005
Circuit | 009007 | [8 empty] | 0 | [21 empty] | 1.2372
Circuit | 149601 |  |  |  |  | 1 | 1 |  |  | 78 | [6 empty] | 14 | 0 | 0 | 0 | 0 | 0 | 1 | 12 | 1 | 0 | 0 | 2.03 | 0.02 | 111.13 | 1 | 0.0078
Circuit | 044001
Circuit | 099001 | [8 empty] | 0 | [21 empty] | 0.0051
Circuit | 002602
Circuit | 064401 |  |  |  | 0 | 1 | 0.832 |  |  | 0 | 3.52 |  |  | 12.74 | 0.28 | 0.28 | 476 | 0 | 0 | 0 | 0 | 0 | 476 | 0 | 0 | 0 | 0 | 323.84 | 1.38 | 234.72 | 0.9925 | 0.7507
Circuit | 007401 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.11 | 0 | 78 | 1
Circuit | 114403 | [8 empty] | 0 | [21 empty] | 0.014
Circuit | 010005 | [9 empty] | 0 |  |  | 0 | 0 | 1
Circuit | 061601 | [8 empty] | 0 | 0.58 |  |  | 0 | 1 | 1.03 | [15 empty] | 0.0011
Circuit | 098502 | [8 empty] | 0 | [21 empty] | 0.1726
Circuit | 040202 | [8 empty] | 0 | [21 empty] | 0.0041
Circuit | 098301 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 390 | 350 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 62.37 | 0.27 | 227.08 | 0.9986 | 0.0317
Circuit | 030402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0 | 94 | 1 | 0.1889
Circuit | 072302 |  |  |  |  | 1 | 0.013 |  |  | 0 | [6 empty] | 1394 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 521.43 | 1.02 | 511.33 | 0.9879 | 1.049
Circuit | 006501 | [9 empty] | 0 |  |  | 0 | 0 | 1
Circuit | 088502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.16 | 0 | 57 | 1 | 0.0072
Circuit | 091601
Circuit | 027901 | [8 empty] | 0 | 6.12 |  |  | 16.9 | 0.36 | 0.36 | [15 empty] | 0.0016
Circuit | 157202 | [8 empty] | 0
Circuit | 161301 |  |  |  | 1
Circuit | 099201 | [8 empty] | 29
Circuit | 067303 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.14 | 0 | 161.77 | 1 | 0.0009
Circuit | 039202 |  |  |  |  | 1 | 1 |  |  | 16 | [6 empty] | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 0.01 | 69.89 | 1 | 0.0708
Circuit | 068502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 143 | 1 | 1.0136
Circuit | 017603 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 11 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1.33 | 0.01 | 107.83 | 1 | 0.001
Circuit | 135601 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 50 | 2 | 0 | 0 | 0 | 0 | 47 | 0 | 1 | 0 | 0 | 7.45 | 0.04 | 166.53 | 0.9998 | 0.0779
Circuit | 005703 | [8 empty] | 0 | [21 empty] | 0.0007
Circuit | 090802 | [8 empty] | 0 | [21 empty] | 0.0008
Circuit | 024301 | [8 empty] | 0 | [21 empty] | 0.0043
Circuit | 167301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 0 | 179.5 | 1 | 0.0042
Circuit | 058604 |  |  | 1 |  | 1 | 0 |  |  | 0 | [6 empty] | 35 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.49 | 0 | 580.73 | 1 | 0.069
Circuit | 013501 |  |  |  |  | 1 | 1 |  |  | 27 | 9.25 |  |  | 22.09 | 0.42 | 0.61 | 131 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 63 | 4.05 | 0.05 | 75.46 | 0.9999 | 0.0004
Circuit | 081802
Circuit | 075705 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.22 | 0 | 81.07 | 1 | 0.0013
Circuit | 036901
Circuit | 010907 | [30 empty] | 0.0043
Circuit | 038002 | [8 empty] | 4 | [21 empty] | 0.0292
Circuit | 061103 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0.51 | 0.01 | 54.54 | 1 | 0.0019
Circuit | 142702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.08 | 0 | 105 | 1 | 0.1222
Circuit | 022803 | [8 empty] | 0 | [21 empty] | 0.3795
Circuit | 029001 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 12 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 9 | 0 | 0 | 4.14 | 0.04 | 93.78 | 0.9999 | 0.0147
Circuit | 033901 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1233 | 1 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 1209 | 0 | 147.97 | 1.04 | 142.45 | 0.9966 | 0.0505
Circuit | 034502 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3.67 | 0.01 | 556.06 | 0.9999 | 0.0311
Circuit | 006203
Circuit | 061501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0.87 | 0.02 | 49.92 | 1
Circuit | 072903 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0 | 96 | 1 | 0.2621
Circuit | 028303 |  |  |  |  | 1 | 1 |  |  | 26 | [6 empty] | 1575 | 415 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 1058 | 68.88 | 1.01 | 68.01 | 0.9984 | 2.0707
Circuit | 017702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 59 | 2 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 14.5 | 0.06 | 231.28 | 0.9997 | 0.0213
Circuit | 019402 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0019
Circuit | 032802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 11 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.5 | 0.01 | 100.22 | 1 | 0.0025
Circuit | 029701 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 1
Circuit | 145102 |  |  |  |  | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 1 | 277 | 1 | 0 | 0 | 0 | 0 | 275 | 0 | 1 | 0 | 0 | 38.38 | 0.17 | 231.42 | 0.9991 | 0.5952
Circuit | 054401 | [8 empty] | 0 | [21 empty] | 0.0013
Circuit | 077401 |  |  | 0 |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.09 | 0 | 94 | 1 | 0.0101
Circuit | 090401
Circuit | 116801 | [8 empty] | 0
Circuit | 122102 |  |  |  |  | 1 | 1 |  |  | 5 | [6 empty] | 6 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.83 | 0 | 197.14 | 1 | 0.0084
Circuit | 053001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 2.08 | 0.01 | 141.31 | 1 | 0.1218
Circuit | 014501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 3.5 | 0.03 | 135.26 | 0.9999 | 0.0011
Circuit | 065701
Circuit | 010927
Circuit | 046301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 369 | 1 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 111 | 1
Circuit | 010203 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.13 | 0 | 139 | 1 | 0.001
Circuit | 039702 | [8 empty] | 0 | [21 empty] | 0.0015
Circuit | 123701 |  |  |  |  | 1 | 1 |  |  | 0 | 16.06 |  |  | 32.99 | 0.49 | 0.58 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 3.05 | 0.02 | 139.12 | 0.9999 | 0.0005
Circuit | 061201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 58.66 | 1 | 0.0467
Circuit | 039803 | [30 empty] | 0.009
Circuit | 159502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 266 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 6.68 | 0.07 | 93.71 | 0.9998 | 0.0155
Circuit | 122502 | [8 empty] | 0 | [21 empty] | 0.1037
Circuit | 114501 | [8 empty] | 0 | 0 |  |  | 0 | 0 | 0 | [15 empty] | 0.0024
Circuit | 095203 |  |  |  |  | 1 | 1 | 1 |  | 65 | [6 empty] | 293 | 5 | 250 | 0 | 0 | 0 | 20 | 1 | 0 | 17 | 0 | 26.19 | 0.24 | 107.07 | 0.9994 | 0.9057
Circuit | 078703 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 8.07 | 0.02 | 385.49 | 0.9998 | 1.0035
Circuit | 063402 | [8 empty] | 0 | 0 |  |  | 8.5 | 0 | 0
Circuit | 090601 | [8 empty] | 0 | [21 empty] | 0.2285
Circuit | 060401 | [8 empty] | 0
Circuit | 103701 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 6 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0 | 68.28 | 1 | 0.0042
Circuit | 036802 |  |  | 0 |  | 1 | 1 |  |  | 0 | 0 |  |  | 7 | 0 | 0 | 198 | 0 | 0 | 46 | 0 | 46 | 106 | 0 | 0 | 0 | 0 | 22.11 | 0.18 | 125.81 | 0.9995 | 0.0566
Circuit | 060904 | [8 empty] | 135 | [21 empty] | 0.0065
Circuit | 039502 | [8 empty] | 0 | [21 empty] | 0.0025
Circuit | 129802 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 169 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 46 | 121 | 11.64 | 0.16 | 72.26 | 0.9997 | 0.047
Circuit | 063701 | [8 empty] | 0
Circuit | 010703
Circuit | 130301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 16.45 | 0.04 | 445.8 | 0.9996 | 0.0123
Circuit | 059401 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2.3 | 0.02 | 152.87 | 0.9999 | 0.0211
Circuit | 077601 | [8 empty] | 0 | [21 empty] | 0.0013
Circuit | 011402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 74 | 56 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 32.12 | 0.21 | 154.51 | 0.9993
Circuit | 093404 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 10 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1.46 | 0.01 | 207.14 | 1 | 0.0028
Circuit | 013801 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.07 | 0.01 | 173.54 | 1 | 0.0038
Circuit | 053801 | [8 empty] | 0 | [6 empty] | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.003
Circuit | 009102 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 181 | 180 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 20.63 | 0.29 | 69.97 | 0.9995 | 0.0049
Circuit | 088201 |  |  |  |  | 1 | 1 |  |  | 11 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.13 | 0 | 88 | 1 | 0.0089
Circuit | 072104 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 117 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.26 | 0.1 | 164.77 | 0.9996 | 0.0018
Circuit | 155501 |  |  |  | 1 | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 0 | 0 | 0 | 15 | 2 | 0 | 0 | 0 | 3.89 | 0.02 | 199.91 | 0.9999 | 0.1581
Circuit | 054003 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 36 | 35 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7.12 | 0.04 | 199.95 | 0.9998 | 0.004
Circuit | 074403
Circuit | 155002 | [8 empty] | 0 | [21 empty] | 0.0021
Circuit | 032201 |  |  | 1 |  | 1 | 1 | 1 |  | 62 | [6 empty] | 38 | 1 | 0 | 0 | 0 | 0 | 14 | 22 | 1 | 0 | 0 | 35.8 | 0.1 | 341.04 | 0.9992 | 0.279
Circuit | 133503 |  |  | 0 |  | 1 | 1 |  |  | 2 | 0 |  |  | 0 | 0 | 0 | 267 | 50 | 0 | 167 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 10.07 | 0.15 | 65.88 | 0.9998 | 0.0046
Circuit | 111202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 34 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 4.46 | 0.02 | 211.13 | 0.9999 | 0.0199
Circuit | 060101 |  |  |  | 1 | 1 | 1 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 27.42 | 0.17 | 164.13 | 0.9994 | 0.0069
Circuit | 104101 |  |  |  | 1 | 1 | 1 |  |  | 2 | [6 empty] | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1.05 | 0.01 | 134.66 | 1 | 0.0052
Circuit | 028902 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.29 | 0 | 303 | 1 | 0.0038
Circuit | 115101 | [8 empty] | 0 | [6 empty] | 90 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0057
Circuit | 021801 |  |  | 0 |  | 1 | 1 |  |  | 1 | 3.58 |  |  | 0 | 1 | 1.79 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.11 | 0 | 95 | 1 | 0.983
Circuit | 021103 |  |  | 1 |  | 1 | 1 |  |  | 0 | [6 empty] | 60 | 0 | 0 | 0 | 0 | 44 | 1 | 0 | 0 | 8 | 7 | 38.34 | 0.11 | 334.81 | 0.9991 | 0.0019
Circuit | 035203 | [30 empty] | 0.058
Circuit | 149902 | [8 empty] | 0 | [21 empty] | 0.0022
MPSC Annual Performance Standard |  | 95% or more | 90% or more completed within 15 business days | 90% or more within 120 minutes in MSAs | 90% or more within 180 minutes in non-MSAs | 90% or more customers restored in 36 hours or less | 90% or more customers restored in 8 hours or less | 90% or more customers restored in 24 hours or less | 90% or more customers restored in 48 hours or less | 6% or less before 2030; 5% or less in 2030 or later

## forestryCircuit
WD# | Amount of Line Cleared (miles) | Quarterly Line Clearing Target (miles) | Quarterly Line Clearing Target (% of internal target met) | Cumulative Line Clearing Target (%) |  | Amount of Line Cleared (miles) | Capital Spend ($000) | O&M Spend ($000) | Quarterly Line Clearing Target (miles) | Quarterly Line Clearing Target (% of internal target met) | Cumulative Line Clearing Target (%)
000202 | 0 | 0.00028186 | 0% | 88.7% | All circuits or areas (month) | 492.2678 | 475 | 7850 | 1332.7918 | 36.94% | 67.91%
000501 | 0 | 0 | 0% | 100% | All circuits or areas (year to date) | 1792.3984 | 1638 | 27842 | 2639.2918 | 67.91% | 67.91%
000601 | 20.3554 | 41.8978 | 48.58% | 55.8%
000705 | 0 | 6.95 | 0% | 0%
000901 | 0 | 22.8 | 0% | 0%
000902 | 0 | 1 | 0% | 0%
001301 | 0 | 18 | 0% | 0%
002002 | 33.8723 | 71.3788 | 47.45% | 66.21%
002303 | 0 | 10.12 | 0% | 0%
003901 | 0.31677 | 1.48 | 21.4% | 100%
003902 | 2.425 | 13.77 | 17.61% | 17.61%
004502 | 0 | 0 | 0% | 100%
004702 | 2.4536 | 20.1 | 12.21% | 12.21%
005401 | 0 | 0 | 0% | 100%
005602 | 0 | 0 | 0% | 100%
006202 | 5.4835 | 0 | 100% | 158.8%
006601 | 0 | 0 | 0% | 100%
006604 | 0 | 0 | 0% | 100%
006703 | 0.1575 | 0 | 100% | 103.6%
006704 | 0 | 0 | 0% | 100%
006705 | 0.070656 | 0 | 100% | 101.7%
006802 | 0 | 0 | 0% | 100%
007302 | 0.82 | 0.82 | 100% | 100%
008002 | 0 | 6.5 | 0% | 0%
008204 | 3.4261 | 16.3455 | 20.96% | 24.66%
008801 | 0 | 0 | 0% | 100%
009902 | 0.1681 | 2.09 | 8.043% | 8.043%
010005 | 0 | 0 | 0% | 100%
010007 | 1.0522 | 0 | 100% | 100%
012402 | 10.8319 | 30.02 | 36.08% | 89.26%
013403 | 0 | 24.16 | 0% | 0%
013501 | 9.2513 | 22.0902 | 41.88% | 60.86%
014502 | 3.5911 | 15.4427 | 23.25% | 54.11%
016201 | 0 | 0.5 | 0% | 0%
016203 | 0 | 21.6 | 0% | 0%
018501 | 0 | 0 | 0% | 0%
018502 | 0.6479 | 8.7044 | 7.443% | 52.97%
021403 | 0 | 2.45 | 0% | 0%
021801 | 3.5793 | 0 | 100% | 179%
022202 | 0 | 3 | 0% | 0%
023101 | 0 | 0 | 0% | 0%
023505 | 0 | 1 | 0% | 0%
023802 | 6.1545 | 15.8554 | 38.82% | 57.72%
024501 | 0 | 0.0021472 | 0% | 100%
024901 | 0.05 | 0.05 | 100% | 100%
025803 | 0 | 1.7378 | 0% | 74.51%
025901 | 0.66183 | 0 | 100% | 102%
026002 | 0 | 2.98 | 0% | 0%
026902 | 0 | 5 | 0% | 0%
027401 | 0.0044936 | 0.00060001 | 748.9% | 87.17%
027901 | 6.1152 | 16.9 | 36.18% | 36.18%
028003 | 0 | 1.98 | 0% | 0%
028302 | 9.546 | 3.1906 | 299.2% | 119.1%
029404 | 0 | 0 | 0% | 0%
029701 | 0 | 0 | 0% | 100%
030301 | 9.4238 | 30.2032 | 31.2% | 33.46%
030603 | 0 | 1.05 | 0% | 0%
030701 | 4.7098 | 4.67 | 100.9% | 100%
031002 | 0 | 0 | 0% | 100%
033103 | 0.76504 | 1.06 | 72.17% | 72.17%
033701 | 6.7164 | 6.6236 | 101.4% | 100.8%
033804 | 3.4475 | 4.03 | 85.55% | 100%
035101 | 0 | 19.16 | 0% | 0%
035201 | 0 | 0.61 | 0% | 0%
036001 | 0.4515 | 0.0014371 | 31417% | 106.9%
036201 | 0 | 0.23 | 0% | 100%
036203 | 0 | 0 | 0% | 100%
036802 | 0 | 7 | 0% | 0%
037303 | 0 | 0.1 | 0% | 0%
037602 | 2.1336 | 0 | 100% | 612.1%
037702 | 0 | 0 | 0% | 100%
038102 | 0.50732 | 0.42376 | 119.7% | 104.9%
038302 | 0 | 0 | 0% | 100%
039002 | 0.13429 | 2.71 | 4.955% | 4.955%
039003 | 0 | 11.3 | 0% | 22.05%
040702 | 5.6463 | 0.31 | 1821% | 188.2%
040802 | 0 | 2.5 | 0% | 0%
041302 | 0 | 0 | 0% | 100%
042001 | 0 | 0 | 0% | 0%
042901 | 0 | 0 | 0% | 0%
043902 | 0 | 0 | 0% | 0%
045403 | 0 | 0.72 | 0% | 0%
046901 | 0 | 2.5 | 0% | 0%
046902 | 0 | 0 | 0% | 0%
048203 | 0 | 1.2143 | 0% | 100%
048301 | 11.5209 | 34.9524 | 32.96% | 48.79%
048502 | 0.43821 | 0 | 100% | 92.82%
049101 | 7.7727 | 15.1874 | 51.18% | 58.13%
049102 | 1.6007 | 0.53528 | 299% | 108.6%
049901 | 1.5296 | 2.0983 | 72.9% | 98.59%
049902 | 13.1383 | 19.2903 | 68.11% | 95.31%
051402 | 0 | 0 | 0% | 0%
051801 | 12.8115 | 19.3517 | 66.2% | 79.2%
052001 | 0 | 0.08 | 0% | 0%
052003 | 6.3 | 10.74 | 58.66% | 61.13%
052004 | 0 | 0.08 | 0% | 0%
052602 | 3.3015 | 4.2309 | 78.03% | 98.32%
053002 | 1.8833 | 5.9767 | 31.51% | 100.2%
054202 | 0.88 | 0 | 100% | 210%
055104 | 0.65055 | 0.0049451 | 13156% | 106.1%
056902 | 0 | 2.75 | 0% | 0%
057303 | 0 | 0 | 0% | 0%
057401 | 4.8608 | 6.1461 | 79.09% | 95.62%
057402 | 13.5568 | 41.9687 | 32.3% | 75.7%
057801 | 0 | 0 | 0% | 0%
058101 | 2.48 | 2.57 | 96.5% | 100%
058102 | 0 | 0 | 0% | 45.9%
058202 | 0 | 3 | 0% | 0%
058302 | 5.5454 | 15.251 | 36.36% | 64.76%
058606 | 0 | 0 | 0% | 100%
059501 | 0 | 0 | 0% | 100%
060101 | 0 | 0 | 0% | 0%
060601 | 6.384 | 29.78 | 21.44% | 56.21%
060801 | 0.64079 | 1.12 | 57.21% | 57.21%
061601 | 0.57977 | 0 | 100% | 102.7%
061704 | 2.4048 | 0.14153 | 1699% | 191%
063102 | 1.89 | 1.89 | 100% | 100%
063402 | 0 | 8.5 | 0% | 0%
063404 | 0 | 6 | 0% | 0%
064401 | 3.5221 | 12.74 | 27.65% | 27.65%
064704 | 5.7 | 12.02 | 47.42% | 51.87%
064801 | 0 | 16.93 | 0% | 0%
066301 | 0 | 0 | 0% | 0%
066601 | 8.2213 | 22.0076 | 37.36% | 42.37%
067402 | 0 | 9.44 | 0% | 0%
067601 | 6.2075 | 25.49 | 24.35% | 31.54%
069803 | 0 | 0.87953 | 0% | 55.99%
070003 | 0.20489 | 5.5547 | 3.689% | 25.18%
070305 | 0 | 6.65 | 0% | 0%
070402 | 0 | 6 | 0% | 0%
070602 | 0 | 4.35 | 0% | 0%
070704 | 0 | 0.98 | 0% | 0%
071702 | 1.3338 | 0 | 100% | 333.3%
072202 | 2.8577 | 10.2273 | 27.94% | 58.28%
072302 | 0 | 0 | 0% | 100%
072401 | 0.12987 | 0 | 100% | 113.6%
072601 | 2.0563 | 2.07 | 99.34% | 100%
072602 | 0.22034 | 0.21966 | 100.3% | 100%
072902 | 2.8019 | 25 | 11.21% | 11.21%
074304 | 0.44953 | 5.1059 | 8.804% | 29.92%
075102 | 0 | 0 | 0% | 0%
075902 | 0 | 2 | 0% | 0%
076901 | 0 | 0.31 | 0% | 0%
078402 | 0 | 0 | 0% | 100%
078405 | 0 | 0 | 0% | 100%
081504 | 0 | 0 | 0% | 100%
082402 | 0 | 10 | 0% | 0%
085702 | 0 | 15.8938 | 0% | 19.78%
085801 | 0 | 0 | 0% | 0%
085803 | 5.97 | 0 | 100% | 260.4%
086801 | 36.9138 | 46.7247 | 79% | 86.97%
088204 | 9.79 | 8.7049 | 112.5% | 100.6%
090101 | 0 | 0 | 0% | 0%
090301 | 0 | 2.89 | 0% | 0%
090304 | 0 | 12.91 | 0% | 0%
090402 | 0 | 6.95 | 0% | 0%
090403 | 0 | 11.82 | 0% | 0%
090503 | 0 | 0 | 0% | 100%
092301 | 0 | 0.84 | 0% | 0%
092302 | 0 | 1.07 | 0% | 0%
093902 | 4.177 | 1.2875 | 324.4% | 117.6%
098204 | 0 | 0 | 0% | 59.55%
100201 | 0 | 0 | 0% | 100%
100204 | 2.57 | 2.57 | 100% | 100%
100901 | 0.65224 | 0.3849 | 169.5% | 128.2%
101204 | 0 | 0 | 0% | 100%
102102 | 0 | 7.74 | 0% | 0%
102201 | 8.1836 | 22.74 | 35.99% | 35.99%
102501 | 0 | 0.002827 | 0% | 100%
103802 | 17.0597 | 8.0403 | 212.2% | 159.2%
105301 | 1.1734 | 1.5 | 78.23% | 78.23%
107503 | 0 | 5 | 0% | 0%
108102 | 0 | 0 | 0% | 0%
109201 | 0 | 0 | 0% | 0%
109202 | 0 | 1.57 | 0% | 0%
112003 | 0 | 0.72 | 0% | 50%
112004 | 1.77 | 1.77 | 100% | 100%
112101 | 0 | 4.63 | 0% | 0%
112103 | 9.8765 | 22.3999 | 44.09% | 83.39%
112202 | 5.413 | 6.7014 | 80.77% | 83.74%
113401 | 3.79 | 0 | 100% | 100%
113601 | 0.29636 | 0 | 100% | 100%
114302 | 10.6508 | 39.112 | 27.23% | 58.15%
114501 | 0 | 0 | 0% | 0%
116501 | 0 | 1.4307 | 0% | 52.76%
117901 | 0 | 3.0981 | 0% | 86.4%
119601 | 0 | 0.81 | 0% | 0%
122705 | 0 | 0 | 0% | 100%
122901 | 0.55878 | 0.0020872 | 26772% | 101%
122902 | 0 | 0 | 0% | 100%
123701 | 16.0595 | 32.9914 | 48.68% | 57.67%
124402 | 0 | 7.05 | 0% | 0%
124701 | 10.4368 | 10.46 | 99.78% | 100%
125203 | 0 | 0 | 0% | 0%
126301 | 0 | 0 | 0% | 100%
127301 | 1.6169 | 0 | 100% | 189.8%
127403 | 13.9176 | 26.3498 | 52.82% | 74.49%
127601 | 8.5439 | 8.5526 | 99.9% | 92.5%
129902 | 4.685 | 30 | 15.62% | 15.62%
131203 | 0 | 0.02 | 0% | 0%
131401 | 4.2795 | 8.0191 | 53.37% | 69.05%
131402 | 0 | 0.009404 | 0% | 81.72%
132201 | 0.031422 | 0 | 100% | 92.93%
133503 | 0 | 0 | 0% | 0%
134702 | 6.4288 | 13.3823 | 48.04% | 79.79%
136602 | 0 | 0 | 0% | 100%
136802 | 3.16 | 3.12 | 101.3% | 101.3%
136803 | 0 | 0 | 0% | 100%
136804 | 1.92 | 3.84 | 50% | 50%
137804 | 0 | 0 | 0% | 25.36%
138301 | 0 | 0 | 0% | 0%
140402 | 0.94 | 0.94 | 100% | 100%
141201 | 0 | 2.9974 | 0% | 86.92%
145102 | 0 | 0 | 0% | 100%
148201 | 0 | 0 | 0% | 100%
148601 | 0 | 0.1619 | 0% | 100%
149301 | 0 | 3.85 | 0% | 0%
149802 | 2.0384 | 2.0472 | 99.57% | 99.95%
150002 | 0 | 3.9 | 0% | 0%
150601 | 0 | 8.5 | 0% | 0%
150602 | 0 | 5.67 | 0% | 0%
150603 | 0 | 0 | 0% | 0%
151201 | 0 | 0.08 | 0% | 99.72%
154101 | 0.39072 | 0.93 | 42.01% | 42.01%
154102 | 0 | 2.5387 | 0% | 75.6%
154201 | 2.2667 | 0 | 100% | 226.7%
154302 | 0 | 4.62 | 0% | 0%
156302 | 0 | 0 | 0% | 100%
156402 | 4.4129 | 4.9647 | 88.88% | 100.5%
157002 | 0 | 0.24 | 0% | 50%
157601 | 3.4496 | 13.07 | 26.39% | 26.39%
158702 | 0 | 0 | 0% | 0%
160401 | 0 | 0 | 0% | 75.6%
163101 | 0 | 0.55131 | 0% | 96.76%
167403 | 0 | 0 | 0% | 100%
168701 | 0 | 4.45 | 0% | 0%
Totals | 492.2678 | 1358.5716 | 36.94% | 67.91%

## Zip Code
RELIABILITY DATA TEMPLATE
Utility: | Consumers Energy Co. |  |  | □ Required Fields
Reporting Month: | 2023-04-30 |  |  | ■ Optional Fields
RELIABILITY DATA REPORTED BY ZIP CODE
| Meter Reading Factor R460.732 (a) | New Service Installation Factor R460.732(b) | Wire Down Relief Factor R460.732 (c) |  | Outage Restoration |  |  |  | CEMI4 | Line Clearing/ Tree Trimming | [5 empty] | Total Customer outages | Outage Causes | [9 empty] | Reliability Metrics (all weather)
[5 empty] | All Conditions R460.732 (d) | Normal Conditions R460.732 (e) | Gray-Sky Conditions R460.732 (f) | Catastrophic Conditions R460.732 (g) | Sustained Interruptions R460.732 (h(i)) | [7 empty] | Equipment | Lightning | Planned | Power Supply | Public | Vegetation | Weather (other than lightning) | Wildlife | Unknown | Other | SAIDI | SAIFI | CAIDI | ASAI | MAIFI
Zip Code | Meter Reading Factor (Percentage) | New Services Installed in 15 Business Days or Less (Percentage) | The percentage of the first responder guarded downed wires that are relieved by an electric utility representative within 120 minutes after notification in MSAs. | The percentage of the first responder guarded downed wires that are relieved by an electric utility representative within 180 minutes after notification in non-MSAs. | Percentage of Customers Restored in 36 Hours or Less | Percentage of Customers Restored in 8 Hours or Less | Percentage of Customers Restored in 24 Hours or Less | Percentage of Customers Restored in 48 Hours or Less | Number of Customers Experiencing 4 or More Sustained Interruptions | Amount of Line Cleared (miles) | Capital Spend ($) | O&M Spend ($) | Quarterly Line Clearing Target (miles) | Quarterly Line Clearing Target (% of internal target met) | Cumulative Line Clearing Target (%) | Total Customer outages | Total number of outages causes by equipment failure | Total number of outages caused by lightning | Total number of planned and forced outages | Total number of outages caused by transmission or generation failure | Total number of outages caused by an act of the public at large | Total number of outages caused by trees | Total number of outages caused by wind, snow, ice, hail, and rain | Total number of outages caued by animal interference | Total number of outages caused by unknonwn causes | Total number of outages caused by other causes | System Average Interruption Duration Index | System Average Interruption Frequency Index | Customer Average Interruption Duration Index (contribution to total CAIDI) | Average Service Availability Index | Momentary Average Interruption Frequency Index
48858 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 650 | 485 | 57 | 1 | 0 | 0 | 89 | 0 | 1 | 17 | 0 | 2.59 | 0.03 | 83.35 | 0.9999 | 0.0921
48601 |  |  |  |  | 1 | 0.714 | 1 |  | 0 | [6 empty] | 209 | 4 | 12 | 115 | 0 | 0 | 32 | 3 | 23 | 20 | 0 | 2.02 | 0.01 | 354.42 | 1 | 0.1833
48161 |  |  |  |  | 1 | 0.992 |  |  | 25 | [6 empty] | 2256 | 2197 | 0 | 0 | 0 | 0 | 22 | 18 | 11 | 0 | 8 | 45.22 | 0.45 | 100.75 | 0.999 | 0.0209
49621 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 935 | 4 | 0 | 278 | 0 | 0 | 653 | 0 | 0 | 0 | 0 | 113.38 | 0.55 | 207.96 | 0.9974 | 0.1519
48463 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0.61 | 0 | 334.18 | 1 | 0.0009
49417 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 81 | 0 | 1 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 3.49 | 0.01 | 254.56 | 0.9999 | 0.0086
49283 |  |  |  |  | 1 |  | 1 |  | 62 | [6 empty] | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 5.63 | 0.01 | 440.19 | 0.9999 | 0.0268
48886 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 57 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 21.42 | 0.05 | 425.11 | 0.9995 | 0.4147
48506 |  |  |  |  | 1 | 0.995 |  |  | 1 | [6 empty] | 255 | 38 | 0 | 34 | 0 | 23 | 22 | 0 | 1 | 1 | 136 | 1.65 | 0.02 | 90.33 | 1 | 0.0387
49623 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 4.81 | 0.01 | 389.91 | 0.9999 | 0.0463
49408 |  |  |  |  | 1 | 0.994 | 1 |  | 1 | [6 empty] | 2331 | 0 | 7 | 0 | 0 | 18 | 2289 | 0 | 1 | 10 | 6 | 81.64 | 0.41 | 199.31 | 0.9981 | 0.2706
49240 |  |  |  |  | 1 | 0.989 | 1 |  | 485 | [6 empty] | 175 | 28 | 0 | 0 | 0 | 0 | 121 | 18 | 4 | 4 | 0 | 6.93 | 0.04 | 175.98 | 0.9998 | 0.0774
48602 |  |  |  |  | 1 | 0.301 | 1 |  | 0 | [6 empty] | 7360 | 5073 | 0 | 1 | 0 | 0 | 150 | 33 | 0 | 2103 | 0 | 212.62 | 0.56 | 382.2 | 0.9951 | 0.9755
48849 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 195 | 14 | 0 | 0 | 0 | 178 | 2 | 0 | 0 | 1 | 0 | 14.74 | 0.09 | 173.43 | 0.9997 | 0.0754
49046 |  |  |  |  | 1 | 1 | 1 |  | 472 | [6 empty] | 531 | 22 | 269 | 0 | 0 | 0 | 195 | 0 | 39 | 0 | 6 | 25.63 | 0.14 | 176.83 | 0.9994 | 0.368
49544 |  |  |  |  | 1 | 1 |  |  | 21 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 1 | 0 | 8 | 0.51 | 0 | 167.68 | 1 | 0.0141
49301 |  |  |  |  | 1 | 0.99 | 1 |  | 39 | [6 empty] | 2289 | 187 | 3 | 1991 | 0 | 0 | 68 | 30 | 6 | 2 | 2 | 7.51 | 0.04 | 209.34 | 0.9998 | 0.0484
49651 |  |  |  |  | 1 | 0.999 | 1 |  | 0 | [6 empty] | 1166 | 1 | 0 | 114 | 0 | 0 | 998 | 14 | 0 | 30 | 9 | 13.07 | 0.18 | 72.15 | 0.9997 | 0.3012
49246 |  |  |  |  | 1 | 1 |  |  | 201 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 1 | 0 | 0 | 1.37 | 0.01 | 166.46 | 1 | 0.1797
48629 |  |  |  |  | 1 | 0.995 |  |  | 0 | [6 empty] | 215 | 2 | 0 | 0 | 0 | 0 | 88 | 0 | 1 | 124 | 0 | 4.23 | 0.03 | 153.02 | 0.9999 | 0.3054
49073 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 65 | 1 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 0 | 671 | 1 | 0.0532
49640 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 569 | 0 | 1 | 0 | 0 | 0 | 566 | 1 | 1 | 0 | 0 | 65.07 | 0.35 | 184.79 | 0.9985 | 0.2896
49024 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0.05 | 0 | 124.25 | 1 | 0.0037
48118 |  |  |  |  | 1 | 1 | 1 |  | 595 | [6 empty] | 48 | 3 | 0 | 0 | 0 | 0 | 19 | 17 | 0 | 9 | 0 | 3.33 | 0.02 | 149.45 | 0.9999 | 0.2417
49053 |  |  |  |  | 1 | 1 | 1 |  | 148 | [6 empty] | 107 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 2 | 0 | 4.87 | 0.03 | 148.01 | 0.9999 | 0.0612
49237 |  |  |  |  | 1 | 1 |  |  | 104 | [6 empty] | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 6.64 | 0.02 | 292.91 | 0.9998 | 0.0207
48632 |  |  |  |  | 1 | 1 |  |  | 272 | [6 empty] | 642 | 340 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 16.61 | 0.14 | 119.24 | 0.9996 | 0.131
48418 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 92 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 41 | 8.69 | 0.05 | 166.52 | 0.9998 | 0.0794
48653 |  |  |  |  | 1 | 0.935 | 1 |  | 0 | [6 empty] | 2237 | 19 | 1 | 0 | 0 | 0 | 505 | 0 | 0 | 0 | 1712 | 15.72 | 0.2 | 79.33 | 0.9996 | 0.2166
49617 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0.58 | 0 | 133.79 | 1 | 0.0354
48817 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 732 | 0 | 0 | 713 | 0 | 0 | 18 | 0 | 0 | 0 | 1 | 0.68 | 0.01 | 111.48 | 1 | 0.6221
48728 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 64 | 2 | 0 | 0 | 46 | 0 | 16 | 0 | 0 | 0 | 0 | 12.46 | 0.04 | 294.96 | 0.9997 | 0.9319
49245 |  |  |  |  | 1 | 1 |  |  | 409 | [6 empty] | 200 | 1 | 0 | 0 | 0 | 0 | 198 | 0 | 1 | 0 | 0 | 7.6 | 0.09 | 84.91 | 0.9998 | 0.0586
49444 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 397 | 0 | 0 | 29 | 0 | 0 | 310 | 0 | 37 | 15 | 6 | 3.2 | 0.03 | 113.04 | 0.9999 | 0.0813
49457 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 4 | 0 | 0 | 0 | 0 | 5 | 0 | 1 | 0 | 0 | 0.35 | 0 | 172.18 | 1 | 0.0081
49420 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0 | 19 | 1 | 0.275
49255 |  |  |  |  | 1 | 0.939 | 1 |  | 371 | [6 empty] | 253 | 2 | 0 | 219 | 0 | 0 | 31 | 0 | 0 | 1 | 0 | 9.37 | 0.04 | 229.85 | 0.9998 | 0.1847
48837 |  |  |  |  | 1 | 1 |  |  | 112 | [6 empty] | 306 | 84 | 0 | 166 | 0 | 0 | 55 | 0 | 0 | 1 | 0 | 1.2 | 0.02 | 77.55 | 1 | 0.017
48137 |  |  |  |  | 1 | 1 |  |  | 176 | [6 empty] | 272 | 0 | 0 | 0 | 0 | 0 | 136 | 136 | 0 | 0 | 0 | 25.99 | 0.17 | 151.84 | 0.9994 | 0.0069
49733 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 31 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 15.58 | 0.1 | 159.34 | 0.9996 | 0.6183
49796 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 243 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 0 | 241.48 | 1.21 | 199.75 | 0.9944 | 0.7662
48145 |  |  |  |  | 1 | 0.625 | 1 |  | 0 | [6 empty] | 65 | 39 | 0 | 0 | 0 | 0 | 25 | 0 | 1 | 0 | 0 | 15.67 | 0.04 | 408.67 | 0.9996 | 0.0071
48614 |  |  |  |  | 1 | 0.99 |  |  | 0 | [6 empty] | 104 | 0 | 0 | 0 | 0 | 0 | 46 | 56 | 0 | 2 | 0 | 37.33 | 0.18 | 212.88 | 0.9991 | 1.0877
49795 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.08 | 0.01 | 13.83 | 1 | 0.2701
49349 |  |  |  |  | 1 | 1 | 1 |  | 68 | [6 empty] | 391 | 94 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 10.71 | 0.2 | 53.84 | 0.9998 | 0.1476
49238 |  |  |  |  | 1 | 0.96 | 1 |  | 2 | [6 empty] | 45 | 22 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 2 | 0 | 10.79 | 0.07 | 157.53 | 0.9998 | 0.9178
48820 |  |  |  |  | 1 | 1 | 1 |  | 6 | [6 empty] | 76 | 7 | 6 | 0 | 0 | 0 | 1 | 61 | 1 | 0 | 0 | 1.39 | 0.01 | 132.9 | 1 | 0.9219
49333 |  |  |  |  | 1 | 0.995 | 1 |  | 187 | [6 empty] | 592 | 21 | 359 | 23 | 0 | 1 | 59 | 0 | 2 | 125 | 2 | 16.44 | 0.11 | 149.31 | 0.9996 | 0.3557
49442 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 600 | 122 | 1 | 47 | 0 | 47 | 369 | 0 | 13 | 1 | 0 | 3.6 | 0.03 | 122.48 | 0.9999 | 0.0625
48743 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 9.21 | 0.03 | 276.25 | 0.9998 | 0.3833
48897 |  |  |  |  | 1 | 0.989 | 1 |  | 8 | [6 empty] | 121 | 68 | 1 | 0 | 0 | 0 | 16 | 0 | 36 | 0 | 0 | 23.82 | 0.16 | 145.07 | 0.9994 | 0.6228
48746 |  |  |  |  | 1 | 0.5 | 1 |  | 0 | [6 empty] | 3 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.93 | 0.01 | 265.33 | 1 | 0.0048
49696 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 346.37 | 1 | 0.7254
49347 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.26 | 0 | 97.41 | 1 | 0.0281
49411 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1.06 | 0 | 308 | 1
49070 |  |  |  |  | 1 | 0.949 | 1 |  | 2 | [6 empty] | 115 | 0 | 1 | 0 | 0 | 0 | 39 | 40 | 0 | 0 | 35 | 19.13 | 0.11 | 172.03 | 0.9996 | 0.0445
48770 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.92 | 0 | 275.5 | 1 | 0.041
48834 |  |  |  |  | 1 | 1 | 1 |  | 102 | [6 empty] | 317 | 14 | 1 | 300 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2.58 | 0.01 | 200.99 | 0.9999 | 0.2745
49508 |  |  |  |  | 1 | 0.992 |  |  | 0 | [6 empty] | 718 | 9 | 0 | 0 | 0 | 6 | 86 | 412 | 126 | 1 | 78 | 5.02 | 0.04 | 121.18 | 0.9999 | 0.0697
49425 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 47 | 1 | 0 | 0 | 0 | 0 | 44 | 1 | 0 | 0 | 1 | 3.39 | 0.03 | 121.92 | 0.9999 | 0.0355
48650 |  |  |  |  | 1 | 0.991 | 1 |  | 40 | [6 empty] | 161 | 59 | 6 | 0 | 0 | 0 | 58 | 0 | 1 | 36 | 1 | 6.89 | 0.04 | 165.45 | 0.9998 | 0.061
49306 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 27 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 22 | 0.19 | 0.01 | 32.16 | 1 | 0.0066
48757 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 26 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7.38 | 0.06 | 132.92 | 0.9998 | 0.0769
49006 |  |  |  |  | 1 | 0.707 |  |  | 10 | [6 empty] | 312 | 296 | 0 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 8.43 | 0.03 | 297.77 | 0.9998 | 0.3914
49322 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1 | 0 | 3.37 | 0.02 | 180.92 | 0.9999 | 0.7826
49271 |  |  |  |  | 1 | 0.569 | 1 |  | 93 | [6 empty] | 76 | 4 | 0 | 0 | 0 | 0 | 46 | 0 | 14 | 12 | 0 | 49.17 | 0.1 | 487.13 | 0.9989 | 0.5378
49633 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 1.32 | 0.01 | 105.85 | 1 | 0.0063
49635 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 230 | 191 | 0 | 0 | 0 | 0 | 2 | 37 | 0 | 0 | 0 | 4.34 | 0.06 | 75.29 | 0.9999 | 0.1227
49274 |  |  |  |  | 1 | 0.938 |  |  | 572 | [6 empty] | 30 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 2 | 0 | 1.73 | 0.01 | 209.97 | 1 | 0.1822
48420 |  |  |  |  | 1 | 1 | 1 |  | 7 | [6 empty] | 54 | 20 | 0 | 0 | 0 | 13 | 0 | 21 | 0 | 0 | 0 | 0.84 | 0.01 | 154.1 | 1 | 0.0686
49066 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 154 | 0 | 153 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 52.3 | 0.41 | 126.67 | 0.9988 | 0.0188
48182 |  |  |  |  | 1 | 0.973 | 1 |  | 1 | [6 empty] | 113 | 9 | 0 | 0 | 0 | 3 | 93 | 2 | 3 | 1 | 2 | 1.88 | 0.01 | 171.32 | 1 | 0.0134
48649 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 1 | 1.94 | 0.01 | 209.04 | 1 | 1.1619
49507 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 60 | 1 | 0 | 4 | 0 | 42 | 1 | 0 | 11 | 0 | 1 | 0.99 | 0 | 252.42 | 1 | 0.4471
49720 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1.81 | 0.01 | 149.99 | 1
49735 |  |  |  |  | 1 | 1 | 1 |  | 128 | [6 empty] | 2761 | 2744 | 1 | 1 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 95.92 | 0.43 | 221.89 | 0.9978 | 0.0542
48442 |  |  |  |  | 1 | 0.944 |  |  | 32 | [6 empty] | 18 | 2 | 0 | 0 | 0 | 0 | 12 | 3 | 0 | 1 | 0 | 0.87 | 0 | 380.2 | 1 | 0.0186
49339 |  |  |  |  | 1 | 1 | 1 |  | 10 | [6 empty] | 14 | 12 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2.52 | 0.02 | 116.92 | 0.9999 | 0.2246
49614 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 169 | 0 | 100 | 0 | 0 | 0 | 0 | 3 | 1 | 13 | 52 | 11.77 | 0.08 | 140.48 | 0.9997 | 0.5736
48740 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 406 | 0 | 3 | 0 | 200 | 0 | 201 | 0 | 0 | 0 | 2 | 14.36 | 0.1 | 150.95 | 0.9997 | 0.139
49040 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 14 | 3 | 6 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 1.3 | 0.01 | 187.28 | 1 | 0.0415
49285 |  |  |  |  | 1 | 1 | 1 |  | 7 | [6 empty] | 27 | 12 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 0 | 2.79 | 0.01 | 225.55 | 0.9999 | 0.0802
48651 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 126 | 11 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 53 | 1.93 | 0.03 | 69.72 | 1 | 0.4186
49051 |  |  |  |  | 1 | 1 |  |  | 140 | [6 empty] | 184 | 74 | 0 | 0 | 0 | 0 | 109 | 0 | 1 | 0 | 0 | 18.88 | 0.18 | 104.14 | 0.9996 | 0.0601
48451 |  |  |  |  | 1 | 0.727 |  |  | 0 | [6 empty] | 64 | 8 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0.41 | 0 | 280.23 | 1 | 0.002
48879 |  |  |  |  | 1 | 1 | 1 |  | 12 | [6 empty] | 134 | 29 | 64 | 1 | 0 | 0 | 1 | 1 | 1 | 37 | 0 | 2.09 | 0.02 | 123.11 | 1 | 0.1974
48628 |  |  |  |  | 1 | 0.091 |  |  | 50 | [6 empty] | 61 | 2 | 0 | 50 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 5.99 | 0.01 | 700.72 | 0.9999 | 0.8779
49445 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 95 | 3 | 0 | 1 | 0 | 0 | 83 | 0 | 7 | 0 | 1 | 0.92 | 0.01 | 98.6 | 1 | 0.0151
49026 |  |  |  |  | 1 |  | 1 |  | 1 | [6 empty] | 53 | 1 | 0 | 42 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 12.15 | 0.05 | 256.25 | 0.9997 | 0.1207
49653 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 21 | 1 | 0 | 0 | 0 | 18 | 2 | 0 | 0 | 0 | 0 | 6.69 | 0.02 | 346.34 | 0.9998 | 0.0083
49461 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 116 | 97 | 0 | 0 | 0 | 0 | 17 | 0 | 1 | 0 | 1 | 2.42 | 0.02 | 102.39 | 0.9999 | 0.0153
48848 |  |  |  |  | 1 | 0.667 | 1 |  | 0 | [6 empty] | 160 | 36 | 78 | 0 | 0 | 0 | 40 | 2 | 3 | 1 | 0 | 16.5 | 0.04 | 386.26 | 0.9996 | 0.2573
49256 |  |  |  |  | 1 | 1 |  |  | 124 | [6 empty] | 219 | 105 | 0 | 0 | 0 | 34 | 0 | 79 | 0 | 1 | 0 | 14.5 | 0.13 | 107.59 | 0.9997 | 0.0775
48861 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0 | 144 | 1 | 0.0147
49270 |  |  |  |  | 1 | 1 |  |  | 8 | [6 empty] | 26 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 0 | 15.77 | 0.08 | 193.48 | 0.9996 | 0.373
49303 |  |  |  |  | 1 | 0 | 1 |  | 1 | [6 empty] | 10 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 3.59 | 0.03 | 111.62 | 0.9999 | 0.0064
48144 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.6 | 0 | 254.94 | 1 | 0.0017
49509 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2646 | 0 | 1951 | 23 | 0 | 290 | 0 | 234 | 102 | 0 | 46 | 15.11 | 0.22 | 67.31 | 0.9997 | 0.0118
49721 |  |  |  |  | 1 | 0.994 |  |  | 0 | [6 empty] | 332 | 2 | 273 | 12 | 0 | 0 | 29 | 0 | 1 | 0 | 15 | 9.8 | 0.06 | 171.75 | 0.9998 | 0.0717
48885 |  |  |  |  | 1 | 0.938 | 1 |  | 16 | [6 empty] | 18 | 12 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | 9.42 | 0.04 | 253.31 | 0.9998 | 0.3616
49679 |  |  |  |  | 1 | 0.9 |  |  | 8 | [6 empty] | 10 | 6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 1 | 2.72 | 0.02 | 154.64 | 0.9999 | 0.0405
49755 |  |  |  |  | 1 | 0.962 |  |  | 0 | [6 empty] | 26 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 19.6 | 0.1 | 205.09 | 0.9995 | 0.0221
48831 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 3 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.4 | 0 | 196.92 | 1 | 0.5034
48859 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.14 | 0.25 | 166.84 | 0.999
48884 |  |  |  |  | 1 | 1 | 1 |  | 6 | [6 empty] | 228 | 125 | 0 | 0 | 0 | 0 | 16 | 27 | 0 | 60 | 0 | 23.73 | 0.11 | 220.09 | 0.9995 | 0.8241
49072 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 55 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4.27 | 0.03 | 124.75 | 0.9999 | 0.0348
49431 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 573 | 43 | 0 | 103 | 0 | 0 | 350 | 0 | 1 | 76 | 0 | 5.64 | 0.05 | 117.57 | 0.9999 | 0.1297
48519 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 129 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4.13 | 0.03 | 130.95 | 0.9999 | 0.1631
48807 |  |  |  |  | 1 |  | 1 |  | 23 | [6 empty] | 6 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 0.02 | 117.68 | 0.9999 | 0.3885
49769 |  |  |  |  | 1 | 0.971 |  |  | 0 | [6 empty] | 348 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 98.7 | 0.49 | 201.66 | 0.9977 | 0.0127
49410 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 94 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 30.54 | 0.32 | 94.21 | 0.9993 | 0.0655
48895 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.28 | 0.03 | 362.16 | 0.9997 | 0.0169
49253 |  |  |  |  | 1 | 0.777 |  |  | 314 | [6 empty] | 354 | 79 | 0 | 0 | 0 | 0 | 265 | 1 | 6 | 2 | 1 | 20.77 | 0.15 | 139.58 | 0.9995 | 0.5986
49071 |  |  |  |  | 1 | 1 | 1 |  | 2 | [6 empty] | 201 | 0 | 0 | 0 | 0 | 0 | 145 | 56 | 0 | 0 | 0 | 11.94 | 0.16 | 76.66 | 0.9997 | 0.3176
49749 |  |  |  |  | 1 | 0.998 |  |  | 0 | [6 empty] | 471 | 13 | 0 | 41 | 0 | 1 | 254 | 102 | 0 | 60 | 0 | 31.41 | 0.17 | 183.13 | 0.9993 | 0.1843
49321 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 364 | 2 | 71 | 0 | 0 | 0 | 262 | 0 | 1 | 1 | 27 | 5.39 | 0.04 | 120.8 | 0.9999 | 0.0078
48818 |  |  |  |  | 1 | 1 |  |  | 10 | [6 empty] | 16 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 6 | 1.11 | 0.01 | 110.63 | 1 | 0.1082
48857 | [8 empty] | 0 | [21 empty] | 0.1752
48460 | [8 empty] | 0 | [21 empty] | 0.0367
49050 | [8 empty] | 0 | [21 empty] | 0.0656
48476 | [8 empty] | 0 | [21 empty] | 0.0141
48806 | [8 empty] | 9 | [21 empty] | 0.0306
49282 | [8 empty] | 0 | [21 empty] | 0.0244
49089 | [8 empty] | 1 | [21 empty] | 0.1002
49254 | [8 empty] | 5 | [21 empty] | 0.0028
48819 | [8 empty] | 111 | [21 empty] | 0.1366
49622 | [8 empty] | 0 | [21 empty] | 0.0176
48724 | [30 empty] | 1.9136
49680
49261 | [8 empty] | 0 | [21 empty] | 0.1138
48836 | [8 empty] | 0
49612 | [8 empty] | 0 | [21 empty] | 0.0018
49320 | [8 empty] | 0 | [21 empty] | 0.0033
48662 | [8 empty] | 0 | [21 empty] | 0.0459
49015 |  |  |  |  | 1 | 1 |  |  | 16 | [6 empty] | 150 | 75 | 0 | 0 | 0 | 0 | 61 | 0 | 13 | 0 | 1 | 1.45 | 0.01 | 130.62 | 1 | 0.0077
49247 |  |  |  |  | 1 | 0.996 | 1 |  | 131 | [6 empty] | 503 | 86 | 0 | 0 | 0 | 0 | 319 | 1 | 56 | 41 | 0 | 26.48 | 0.17 | 153.82 | 0.9994 | 0.2201
48449 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 26 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 25 | 0 | 0 | 2.19 | 0.02 | 122.24 | 0.9999 | 0.0269
49262 |  |  |  |  | 1 | 1 |  |  | 118 | [6 empty] | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 7 | 41 | 25.76 | 0.17 | 148.16 | 0.9994 | 0.1724
49030 |  |  |  |  | 1 | 0.957 | 1 |  | 117 | [6 empty] | 24 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 6 | 14 | 2.05 | 0.02 | 127.68 | 1 | 0.0147
49224 |  |  |  |  | 1 | 0.551 | 1 |  | 873 | [6 empty] | 1192 | 360 | 26 | 17 | 0 | 1 | 340 | 447 | 0 | 0 | 1 | 66.73 | 0.18 | 363.08 | 0.9985 | 0.3128
49629 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1945 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1943 | 0 | 204.48 | 0.98 | 209.53 | 0.9953 | 0.0281
48730 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 92.76 | 1 | 0.1552
49449 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 67 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 66 | 0 | 2.41 | 0.03 | 84.86 | 0.9999 | 0.0097
48509 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 48 | 24 | 0 | 14 | 0 | 0 | 1 | 6 | 0 | 0 | 3 | 0.49 | 0.01 | 67.27 | 1 | 0.1999
49664 |  |  |  |  | 1 | 0.994 |  |  | 0 | [6 empty] | 345 | 181 | 0 | 0 | 0 | 0 | 148 | 16 | 0 | 0 | 0 | 25.66 | 0.16 | 162.9 | 0.9994 | 0.5237
48911 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 3.42 | 0.03 | 110.46 | 0.9999 | 0.0505
48708 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 6 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.38 | 0 | 158.92 | 1 | 0.0267
49419 |  |  |  |  | 1 | 1 | 1 |  | 7 | [6 empty] | 156 | 22 | 26 | 0 | 0 | 0 | 12 | 94 | 0 | 2 | 0 | 7.74 | 0.05 | 171.93 | 0.9998 | 0.0113
48703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 282 | 4 | 0 | 0 | 0 | 0 | 275 | 0 | 1 | 2 | 0 | 20.58 | 0.09 | 229.41 | 0.9995 | 0.3152
48842 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 528 | 2 | 156 | 366 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2.15 | 0.02 | 126.17 | 1 | 0.2264
48841 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.57 | 0.01 | 111.01 | 1 | 1.3152
49288 |  |  |  |  | 1 | 0.603 | 1 |  | 42 | [6 empty] | 144 | 71 | 0 | 0 | 0 | 5 | 50 | 0 | 0 | 18 | 0 | 90.26 | 0.21 | 429.99 | 0.9979 | 0.4679
49434 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 308 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 426.23 | 0.97 | 437.3 | 0.9901 | 0.6013
49619 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 47.78 | 0.8 | 59.53 | 0.9989 | 0.01
48722 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 26 | 1 | 24 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2.45 | 0.02 | 153.57 | 0.9999 | 0.0012
49014 |  |  |  |  | 1 | 1 | 1 |  | 86 | [6 empty] | 499 | 3 | 0 | 0 | 0 | 1 | 322 | 126 | 0 | 0 | 47 | 7.7 | 0.05 | 156.85 | 0.9998 | 0.0046
49310 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 201.09 | 1 | 0.0079
49665 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 357 | 181 | 1 | 0 | 0 | 0 | 32 | 1 | 1 | 0 | 141 | 36.79 | 0.25 | 148.2 | 0.9991 | 0.5633
49017 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 160 | 4 | 13 | 0 | 0 | 0 | 108 | 33 | 2 | 0 | 0 | 2.52 | 0.02 | 160.24 | 0.9999 | 0.4861
49080 |  |  |  |  | 1 | 1 | 1 |  | 82 | [6 empty] | 937 | 3 | 1 | 0 | 0 | 0 | 895 | 32 | 3 | 1 | 2 | 34.84 | 0.12 | 281.91 | 0.9992 | 0.2376
49036 |  |  |  |  | 1 | 1 | 1 |  | 1175 | [6 empty] | 4093 | 1 | 0 | 3629 | 0 | 268 | 33 | 22 | 0 | 106 | 34 | 10.55 | 0.07 | 155.48 | 0.9998 | 0.1691
49663 |  |  |  |  | 1 | 1 | 1 |  | 174 | [6 empty] | 77 | 14 | 1 | 0 | 0 | 0 | 59 | 2 | 0 | 1 | 0 | 6.33 | 0.02 | 255.9 | 0.9999 | 0.1546
49727 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0.07 | 0 | 18.94 | 1 | 0.0016
49092 |  |  |  |  | 1 | 1 |  |  | 58 | [6 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0.65 | 0.01 | 76.65 | 1 | 0.0615
48619 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76 | 0 | 414 | 1 | 0.4144
48705 |  |  |  |  | 1 | 0.993 |  |  | 0 | [6 empty] | 757 | 21 | 0 | 0 | 622 | 0 | 111 | 0 | 0 | 3 | 0 | 17.03 | 0.16 | 109.46 | 0.9996 | 0.5801
49323 |  |  |  |  | 1 | 1 | 0.988 |  | 14 | [6 empty] | 1851 | 1401 | 0 | 0 | 0 | 0 | 367 | 46 | 1 | 36 | 0 | 128.51 | 0.56 | 230.64 | 0.997 | 0.3055
49332 |  |  |  |  | 1 | 0.988 |  |  | 28 | [6 empty] | 84 | 2 | 0 | 1 | 0 | 0 | 63 | 2 | 0 | 16 | 0 | 2.51 | 0.03 | 74.67 | 0.9999 | 0.3753
49688 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 106 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 67 | 16.96 | 0.11 | 155.86 | 0.9996 | 0.0062
48811 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 45 | 25 | 2 | 0 | 0 | 0 | 2 | 8 | 0 | 8 | 0 | 3.61 | 0.03 | 119.56 | 0.9999 | 0.0369
49230 |  |  |  |  | 1 | 1 | 1 |  | 851 | [6 empty] | 845 | 115 | 0 | 1 | 0 | 0 | 493 | 80 | 0 | 0 | 156 | 20.05 | 0.12 | 164.54 | 0.9995 | 0.2522
48867 |  |  |  |  | 1 | 0.964 | 1 |  | 0 | [6 empty] | 309 | 7 | 5 | 205 | 0 | 0 | 59 | 27 | 1 | 4 | 1 | 0.95 | 0.01 | 125.5 | 1 | 0.5278
49401 |  |  |  |  | 1 | 0.997 |  |  | 0 | [6 empty] | 348 | 2 | 0 | 18 | 0 | 16 | 2 | 0 | 249 | 0 | 61 | 3.52 | 0.04 | 98.08 | 0.9999 | 0.0164
49685 |  |  |  |  | 1 | 0.995 | 1 |  | 0 | [6 empty] | 217 | 205 | 2 | 0 | 0 | 0 | 9 | 0 | 1 | 0 | 0 | 5.36 | 0.05 | 111.29 | 0.9999 | 1.1462
48621 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 0.02 | 65.14 | 1
49402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.53 | 0.02 | 94.21 | 1 | 0.0626
48847 |  |  |  |  | 1 | 1 | 1 |  | 142 | [6 empty] | 104 | 5 | 2 | 0 | 0 | 13 | 0 | 44 | 40 | 0 | 0 | 4.32 | 0.03 | 129.71 | 0.9999 | 0.064
48827 |  |  |  |  | 1 | 0.785 | 1 |  | 0 | [6 empty] | 546 | 412 | 1 | 0 | 0 | 0 | 14 | 0 | 88 | 31 | 0 | 44.69 | 0.14 | 325.88 | 0.999 | 0.0598
48721 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 862 | 0 | 0 | 0 | 429 | 0 | 429 | 0 | 0 | 3 | 1 | 146.66 | 0.97 | 151.4 | 0.9966 | 0.1812
48158 |  |  |  |  | 1 | 1 | 1 |  | 116 | [6 empty] | 144 | 4 | 0 | 11 | 0 | 0 | 32 | 27 | 0 | 52 | 18 | 5.61 | 0.04 | 126.46 | 0.9999 | 0.3609
49648 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 169.81 | 0.81 | 209.31 | 0.9961
48638 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 4979 | 402 | 400 | 17 | 0 | 0 | 24 | 0 | 8 | 4126 | 2 | 117.48 | 0.74 | 158.84 | 0.9973 | 0.1468
48910 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.16 | 0.01 | 437.08 | 0.9999
49082 |  |  |  |  | 1 | 1 | 1 |  | 480 | [6 empty] | 731 | 251 | 0 | 32 | 0 | 1 | 378 | 69 | 0 | 0 | 0 | 29.75 | 0.2 | 147.56 | 0.9993 | 0.1581
49683 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.31 | 0.03 | 11.08 | 1 | 3.4528
48840 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 862 | 1 | 0 | 1 | 0 | 0 | 859 | 0 | 0 | 1 | 0 | 17.26 | 0.13 | 132.96 | 0.9996 | 0.1401
49649 |  |  |  |  | 1 | 0.976 |  |  | 0 | [6 empty] | 82 | 76 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 0 | 5.55 | 0.03 | 205.38 | 0.9999 | 0.0023
49525 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 39 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 1 | 0 | 0.33 | 0 | 124.02 | 1 | 0.0562
49037 |  |  |  |  | 1 | 0.737 |  |  | 1 | [6 empty] | 633 | 11 | 0 | 48 | 0 | 545 | 28 | 0 | 0 | 0 | 1 | 12.86 | 0.05 | 238.64 | 0.9997 | 0.4486
48436 |  |  |  |  | 1 | 0.892 |  |  | 0 | [6 empty] | 37 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 30 | 0 | 5.98 | 0.02 | 247.25 | 0.9999 | 0.0203
49656 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 51 | 1 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 7.88 | 0.06 | 122.05 | 0.9998 | 0.0658
49094 |  |  |  |  | 1 | 0 | 1 |  | 0 | [6 empty] | 42 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 1 | 0 | 0 | 6.09 | 0.05 | 120.1 | 0.9999 | 0.3249
49670 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.43 | 0 | 390 | 1 | 0.018
49048 |  |  |  |  | 1 | 0.867 |  |  | 92 | [6 empty] | 113 | 2 | 50 | 0 | 0 | 38 | 8 | 0 | 0 | 0 | 15 | 3.43 | 0.01 | 371.79 | 0.9999 | 0.0113
48507 |  |  |  |  | 1 | 0.996 | 1 |  | 0 | [6 empty] | 559 | 403 | 1 | 1 | 0 | 0 | 0 | 39 | 0 | 35 | 80 | 3.2 | 0.04 | 89.83 | 0.9999 | 0.0107
49079 |  |  |  |  | 1 | 1 | 1 |  | 17 | [6 empty] | 271 | 5 | 0 | 0 | 0 | 0 | 47 | 219 | 0 | 0 | 0 | 41.6 | 0.37 | 113.74 | 0.999 | 0.637
49452 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 3.97 | 0.03 | 120.74 | 0.9999 | 0.0164
48762 |  |  |  |  | 1 | 1 |  |  | 3 | [6 empty] | 2124 | 373 | 0 | 0 | 1121 | 0 | 628 | 0 | 0 | 1 | 1 | 102.09 | 0.87 | 117.16 | 0.9976 | 0.1772
49428 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 337 | 12 | 0 | 11 | 0 | 0 | 0 | 190 | 4 | 120 | 0 | 4.4 | 0.03 | 154.58 | 0.9999 | 0.002
48611 |  |  |  |  | 1 | 1 | 1 |  | 18 | [6 empty] | 26 | 7 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.3 | 0 | 118.7 | 1 | 0.0347
48761 |  |  |  |  | 1 | 0.995 | 1 |  | 0 | [6 empty] | 187 | 15 | 1 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 28.3 | 0.13 | 224.14 | 0.9993 | 0.293
48642 |  |  |  |  | 1 | 0.168 |  |  | 3203 | [6 empty] | 3315 | 2 | 0 | 3214 | 0 | 0 | 85 | 0 | 0 | 1 | 13 | 3.8 | 0.01 | 623.41 | 0.9999 | 0.5098
49269 |  |  |  |  | 1 | 0.704 |  |  | 67 | [6 empty] | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.84 | 0.03 | 451.16 | 0.9997 | 0.0351
49643 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.5 | 0 | 172.65 | 1 | 0.0582
49344 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 0 | 1 | 0 | 0.6 | 0 | 188.17 | 1 | 0.0149
49642 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 91 | 1 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 36.63 | 0.13 | 279.73 | 0.9992 | 0.2561
49453 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 79 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 0 | 0 | 7 | 2.44 | 0.03 | 88.29 | 0.9999 | 0.1187
49232 |  |  |  |  | 1 | 0.838 |  |  | 144 | [6 empty] | 160 | 37 | 0 | 0 | 0 | 1 | 0 | 26 | 0 | 29 | 67 | 28.09 | 0.11 | 255.94 | 0.9993 | 0.4239
48654 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 187 | 5 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 13.88 | 0.08 | 167.54 | 0.9997 | 0.0682
49064 |  |  |  |  | 1 | 1 | 1 |  | 93 | [6 empty] | 195 | 0 | 7 | 0 | 0 | 0 | 186 | 2 | 0 | 0 | 0 | 28.09 | 0.12 | 226.77 | 0.9993 | 0.0781
48612 |  |  |  |  | 1 | 1 | 1 |  | 13 | [6 empty] | 49 | 6 | 0 | 0 | 0 | 18 | 13 | 0 | 0 | 12 | 0 | 0.66 | 0.01 | 90.63 | 1 | 0.0519
48866 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 73 | 1 | 0 | 0 | 0 | 0 | 42 | 1 | 0 | 0 | 29 | 3.94 | 0.03 | 114.65 | 0.9999 | 0.1049
49738 |  |  |  |  | 1 | 0.962 | 1 |  | 0 | [6 empty] | 469 | 34 | 1 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 416 | 7.74 | 0.14 | 56.84 | 0.9998 | 0.2754
49331 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 536 | 12 | 0 | 0 | 0 | 33 | 329 | 1 | 1 | 160 | 0 | 9.59 | 0.11 | 89.81 | 0.9998 | 0.5305
49316 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 214 | 19 | 0 | 1 | 0 | 0 | 58 | 129 | 4 | 2 | 1 | 5.03 | 0.02 | 250.22 | 0.9999 | 0.0489
48637 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 76 | 1 | 1 | 0 | 0 | 0 | 61 | 3 | 0 | 0 | 10 | 3.49 | 0.05 | 77.21 | 0.9999 | 0.0232
48748 |  |  |  |  | 1 | 0.929 |  |  | 0 | [6 empty] | 28 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 23 | 1.75 | 0.01 | 131.35 | 1 | 0.0413
49032 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 15 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 13 | 0 | 1.37 | 0.01 | 109.07 | 1 | 0.4268
49012 |  |  |  |  | 1 | 1 | 1 |  | 5 | [6 empty] | 55 | 1 | 0 | 24 | 0 | 0 | 24 | 0 | 6 | 0 | 0 | 2.52 | 0.02 | 137.7 | 0.9999 | 0.2823
49534 |  |  |  |  | 1 | 0.989 |  |  | 0 | [6 empty] | 355 | 3 | 0 | 0 | 0 | 0 | 180 | 106 | 2 | 17 | 47 | 7.87 | 0.03 | 255.35 | 0.9998 | 0.0255
48872 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 252 | 192 | 6 | 0 | 0 | 0 | 52 | 2 | 0 | 0 | 0 | 14.46 | 0.08 | 185.86 | 0.9997 | 0.1053
49346 |  |  |  |  | 1 | 0.992 | 1 |  | 1 | [6 empty] | 169 | 4 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 16.87 | 0.09 | 189.95 | 0.9996 | 0.2806
48737 |  |  |  |  | 1 | 0.864 | 1 |  | 0 | [6 empty] | 64 | 2 | 13 | 3 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 4.94 | 0.04 | 135.24 | 0.9999 | 0.0246
48880 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 123 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 10.3 | 0.08 | 128.82 | 0.9998 | 0.1027
49712 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0.17 | 0 | 78.77 | 1 | 0.172
49277 |  |  |  |  | 1 | 0.506 | 1 |  | 38 | [6 empty] | 156 | 35 | 1 | 0 | 0 | 0 | 81 | 0 | 1 | 0 | 38 | 33.53 | 0.11 | 303.31 | 0.9992 | 0.0588
49268 |  |  |  |  | 1 | 1 |  |  | 75 | [6 empty] | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0.04 | 111.94 | 0.9999 | 0.9535
49263 |  |  |  |  | 1 | 1 |  |  | 25 | [6 empty] | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 198.93 | 1 | 198.93 | 0.9954
49659 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 245 | 1 | 241 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 21.26 | 0.13 | 163.29 | 0.9995 | 0.6132
48850 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.01 | 0.01 | 201.9 | 1 | 0.6866
48864 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.07 | 0 | 196.69 | 1 | 0.0136
49451 |  |  |  |  | 1 | 0.96 | 1 |  | 1 | [6 empty] | 95 | 1 | 1 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 47 | 3.78 | 0.04 | 85.58 | 0.9999 | 0.1914
48655 |  |  |  |  | 1 | 0.999 | 1 |  | 0 | [6 empty] | 781 | 42 | 2 | 0 | 0 | 0 | 599 | 88 | 0 | 1 | 49 | 40.9 | 0.27 | 152.66 | 0.9991 | 1.0816
48873 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45 | 0 | 268 | 1 | 0.0539
49060 |  |  |  |  | 1 | 1 | 1 |  | 47 | [6 empty] | 122 | 0 | 8 | 0 | 0 | 0 | 38 | 0 | 76 | 0 | 0 | 13.83 | 0.11 | 126.81 | 0.9997 | 0.2002
48423 |  |  |  |  | 1 | 0.199 | 1 |  | 0 | [6 empty] | 169 | 3 | 0 | 32 | 0 | 0 | 39 | 1 | 0 | 2 | 92 | 10.48 | 0.01 | 1292.76 | 0.9998 | 0.0252
48623 |  |  |  |  | 1 | 0.993 | 1 |  | 0 | [6 empty] | 753 | 634 | 0 | 0 | 0 | 84 | 31 | 2 | 0 | 1 | 1 | 22.59 | 0.12 | 192.18 | 0.9995 | 0.7129
49546 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 528 | 10 | 0 | 53 | 0 | 1 | 379 | 3 | 81 | 1 | 0 | 2.48 | 0.03 | 79.42 | 0.9999 | 0.011
49056 |  |  |  |  | 1 | 0.974 | 1 |  | 485 | [6 empty] | 800 | 8 | 16 | 382 | 0 | 0 | 392 | 0 | 0 | 1 | 1 | 38.88 | 0.16 | 243.51 | 0.9991 | 0.3419
48851 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 159 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 40.6 | 0.2 | 204.52 | 0.9991 | 0.1411
49406 |  |  |  |  | 1 | 0.089 |  |  | 2 | [6 empty] | 56 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 22.75 | 0.04 | 511.82 | 0.9995 | 0.3198
49248 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 45 | 6 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 8.35 | 0.12 | 67.18 | 0.9998 | 1.163
48749 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.33 | 0 | 133.53 | 1 | 0.0147
49686 |  |  |  |  | 1 | 0.886 | 1 |  | 0 | [6 empty] | 71 | 10 | 0 | 0 | 0 | 1 | 58 | 0 | 1 | 1 | 0 | 3.38 | 0.01 | 267.97 | 0.9999 | 0.7629
49276 |  |  |  |  | 1 | 1 |  |  | 4 | [6 empty] | 449 | 365 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 251.02 | 1.21 | 207.98 | 0.9942 | 0.1989
48876 |  |  |  |  | 1 | 1 |  |  | 384 | [6 empty] | 73 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.54 | 0.04 | 127.09 | 0.9999 | 0.133
49454 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 28 | 2 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 21 | 0 | 1.53 | 0.02 | 65.27 | 1
49264 |  |  |  |  | 1 | 0.852 | 1 |  | 40 | [6 empty] | 311 | 183 | 0 | 0 | 0 | 0 | 80 | 0 | 8 | 0 | 40 | 80.87 | 0.43 | 188.25 | 0.9981 | 0.0691
48433 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 461 | 214 | 0 | 0 | 0 | 0 | 148 | 18 | 13 | 0 | 68 | 7 | 0.04 | 188.16 | 0.9998 | 0.078
49341 |  |  |  |  | 1 | 1 | 1 |  | 244 | [6 empty] | 2961 | 196 | 99 | 0 | 0 | 0 | 453 | 1313 | 3 | 49 | 848 | 22.65 | 0.18 | 126.23 | 0.9995 | 0.3204
49343 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 110 | 14 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 27 | 0 | 10.08 | 0.05 | 217 | 0.9998 | 0.1381
49309 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 20 | 1 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 56.11 | 1 | 56.11 | 0.9987 | 0.7
49418 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 117 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 83 | 0.81 | 0.01 | 102.67 | 1 | 0.0129
49279 |  |  |  |  | 1 | 1 |  |  | 4 | [6 empty] | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 23 | 0 | 6.91 | 0.07 | 97.69 | 0.9998 | 0.0909
48706 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 504 | 367 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 1 | 97 | 2.82 | 0.05 | 62.24 | 0.9999 | 0.0263
48871 | [8 empty] | 0 | [21 empty] | 0.0009
49637 | [8 empty] | 0
49093 | [8 empty] | 7 | [21 empty] | 0.0208
49705
49636 | [8 empty] | 0 | [21 empty] | 0.3112
49729 | [8 empty] | 0
48411 | [30 empty] | 0.04
48169 | [8 empty] | 0 | [21 empty] | 0.0025
48607 | [8 empty] | 0 | [21 empty] | 0.2694
48874 | [8 empty] | 0
48894 | [30 empty] | 0.0508
48763 | [8 empty] | 0 | [21 empty] | 0.1061
48912
49706 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1.55 | 0.01 | 166.74 | 1 | 0.0202
49221 |  |  |  |  | 1 | 0.985 |  |  | 325 | [6 empty] | 1979 | 75 | 0 | 0 | 0 | 26 | 3 | 95 | 3 | 1692 | 85 | 17.1 | 0.12 | 143.14 | 0.9996 | 0.218
48624 |  |  |  |  | 1 | 1 | 1 |  | 66 | [6 empty] | 3256 | 70 | 231 | 1 | 0 | 0 | 2339 | 0 | 0 | 4 | 611 | 44 | 0.24 | 181.7 | 0.999 | 0.6637
48889 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.39 | 0 | 222 | 1
49342 |  |  |  |  | 1 | 1 | 1 |  | 17 | [6 empty] | 53 | 0 | 2 | 1 | 0 | 0 | 48 | 0 | 2 | 0 | 0 | 3.59 | 0.06 | 60.37 | 0.9999 | 0.2011
48457 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 159 | 47 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 7.57 | 0.04 | 178.33 | 0.9998 | 0.2231
49326 |  |  |  |  | 1 | 0.998 | 1 |  | 77 | [6 empty] | 724 | 37 | 102 | 0 | 0 | 0 | 582 | 2 | 0 | 1 | 0 | 93.71 | 0.4 | 234.26 | 0.9978 | 0.5022
49202 |  |  |  |  | 1 | 1 | 1 |  | 37 | [6 empty] | 83 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 56 | 0.85 | 0.01 | 106.75 | 1 | 0.1246
49667 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.36 | 0 | 87.73 | 1 | 0.2531
49690 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1708 | 2 | 0 | 1463 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 23.33 | 0.11 | 208.88 | 0.9995 | 0.5301
49689 |  |  |  |  | 1 | 1 |  |  | 17 | [6 empty] | 510 | 0 | 1 | 0 | 0 | 0 | 508 | 0 | 0 | 0 | 1 | 32.82 | 0.32 | 103.73 | 0.9992 | 0.696
49437 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 14 | 1 | 0 | 11 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.12 | 0 | 117.96 | 1 | 0.4143
49660 |  |  |  |  | 1 | 1 | 1 |  | 56 | [6 empty] | 114 | 5 | 0 | 0 | 0 | 0 | 89 | 11 | 4 | 0 | 5 | 1.19 | 0.01 | 90.89 | 1 | 0.0977
49251 |  |  |  |  | 1 | 1 | 1 |  | 25 | [6 empty] | 230 | 209 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 26.6 | 0.08 | 322.13 | 0.9994 | 0.0083
48610 |  |  |  |  | 1 | 1 |  |  | 26 | [6 empty] | 284 | 0 | 25 | 1 | 0 | 0 | 257 | 0 | 0 | 1 | 0 | 9.9 | 0.09 | 110.35 | 0.9998 | 1.1451
49345 |  |  |  |  | 1 | 1 | 1 |  | 42 | [6 empty] | 591 | 2 | 284 | 0 | 0 | 0 | 110 | 155 | 3 | 37 | 0 | 12.54 | 0.09 | 133.57 | 0.9997 | 0.2058
49423 |  |  |  |  | 1 | 0.984 | 1 |  | 72 | [6 empty] | 711 | 68 | 195 | 0 | 0 | 0 | 438 | 3 | 0 | 0 | 7 | 31.57 | 0.15 | 213.29 | 0.9993 | 0.0895
48822 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 3.68 | 0.04 | 99.96 | 0.9999 | 0.0013
49756 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 70 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 530.03 | 0.88 | 605.75 | 0.9877
49055 |  |  |  |  | 1 | 0.992 | 1 |  | 278 | [6 empty] | 453 | 176 | 1 | 0 | 0 | 0 | 50 | 52 | 174 | 0 | 0 | 32.53 | 0.22 | 144.97 | 0.9992 | 0.0877
49001 |  |  |  |  | 1 | 0.999 | 1 |  | 4 | [6 empty] | 1537 | 1 | 1009 | 45 | 0 | 0 | 0 | 480 | 0 | 1 | 1 | 16.96 | 0.14 | 121.83 | 0.9996 | 0.1823
49028 |  |  |  |  | 1 | 1 | 1 |  | 264 | [6 empty] | 409 | 2 | 0 | 207 | 0 | 175 | 14 | 9 | 0 | 1 | 1 | 10.12 | 0.06 | 169.32 | 0.9998 | 0.0568
48813 |  |  |  |  | 1 | 1 | 1 |  | 93 | [6 empty] | 680 | 12 | 69 | 0 | 0 | 69 | 0 | 90 | 2 | 437 | 1 | 6.04 | 0.08 | 79.78 | 0.9999 | 0.1943
49033 |  |  |  |  | 1 | 1 |  |  | 26 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0 | 216.32 | 1 | 0.0023
48855 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0 | 347 | 1 | 0.0704
48609 |  |  |  |  | 1 | 0.991 |  |  | 0 | [6 empty] | 158 | 80 | 0 | 43 | 0 | 0 | 4 | 1 | 29 | 1 | 0 | 3.58 | 0.02 | 191.39 | 0.9999 | 0.4248
48429 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 1 | 0 | 10 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.15 | 0 | 214.07 | 1 | 0.0643
48616 |  |  |  |  | 1 | 0.989 | 1 |  | 0 | [6 empty] | 101 | 2 | 1 | 0 | 0 | 0 | 96 | 1 | 0 | 1 | 0 | 4.93 | 0.03 | 174.81 | 0.9999 | 1.0793
49644 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 76 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 192.34 | 1.85 | 103.76 | 0.9955 | 4.7561
48829 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.52 | 0 | 112.72 | 1 | 0.0294
49330 |  |  |  |  | 1 | 0.99 | 1 |  | 228 | [6 empty] | 128 | 1 | 0 | 0 | 0 | 0 | 98 | 0 | 1 | 24 | 4 | 5.87 | 0.06 | 93.75 | 0.9999 | 0.0607
49464 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 969 | 174 | 10 | 721 | 0 | 44 | 1 | 0 | 4 | 8 | 7 | 6.3 | 0.06 | 110.67 | 0.9999 | 0.0094
48734 |  |  |  |  | 1 | 0.529 |  |  | 0 | [6 empty] | 21 | 7 | 0 | 4 | 0 | 0 | 0 | 8 | 1 | 1 | 0 | 1.42 | 0 | 332.33 | 1 | 0.047
48661 |  |  |  |  | 1 | 0.976 |  |  | 0 | [6 empty] | 123 | 5 | 74 | 0 | 0 | 0 | 30 | 0 | 1 | 13 | 0 | 2.69 | 0.02 | 165.84 | 0.9999 | 0.4122
49337 |  |  |  |  | 1 | 1 | 1 |  | 668 | [6 empty] | 1612 | 16 | 1 | 0 | 0 | 0 | 1559 | 0 | 0 | 36 | 0 | 19.93 | 0.28 | 71.34 | 0.9995 | 0.3475
48875 |  |  |  |  | 1 | 0.667 | 1 |  | 0 | [6 empty] | 91 | 1 | 87 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 9.24 | 0.12 | 79.99 | 0.9998 | 0.2576
48765 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 0 | 474 | 1 | 0.0853
49011 |  |  |  |  | 1 | 1 | 1 |  | 141 | [6 empty] | 12 | 1 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 1.39 | 0.01 | 137.93 | 1 | 0.0059
48659 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 32 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2.35 | 0.02 | 130.21 | 0.9999 | 0.4741
49319 |  |  |  |  | 1 | 1 | 1 |  | 35 | [6 empty] | 1767 | 422 | 20 | 0 | 0 | 0 | 270 | 1 | 3 | 1 | 1050 | 21.63 | 0.26 | 83.35 | 0.9995 | 0.5085
49249 |  |  |  |  | 1 | 1 |  |  | 38 | [6 empty] | 27 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 7 | 0 | 7 | 1.14 | 0.01 | 86.35 | 1 | 0.0225
49404 |  |  |  |  | 1 | 0.997 | 1 |  | 2 | [6 empty] | 564 | 1 | 245 | 0 | 0 | 290 | 21 | 5 | 1 | 1 | 0 | 22.2 | 0.15 | 146.17 | 0.9995 | 0.0929
49265 |  |  |  |  | 1 | 0.936 |  |  | 160 | [6 empty] | 141 | 5 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 23.08 | 0.06 | 377.83 | 0.9995 | 0.1096
49091 |  |  |  |  | 1 | 1 |  |  | 181 | [6 empty] | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.16 | 0 | 107.1 | 1 | 0.1424
48865 |  |  |  |  | 1 | 1 |  |  | 372 | [6 empty] | 832 | 5 | 0 | 760 | 0 | 0 | 57 | 0 | 0 | 10 | 0 | 5.58 | 0.09 | 63.28 | 0.9999 | 0.2987
49266 |  |  |  |  | 1 | 0.981 |  |  | 1035 | [6 empty] | 52 | 42 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 6.04 | 0.04 | 171.44 | 0.9999 | 0.0765
49008 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 762 | 18 | 0 | 1 | 0 | 0 | 0 | 743 | 0 | 0 | 0 | 16.74 | 0.1 | 171.51 | 0.9996 | 0.2256
49272 |  |  |  |  | 1 | 1 | 1 |  | 2 | [6 empty] | 281 | 255 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 1 | 0 | 76.27 | 0.24 | 318.64 | 0.9982 | 0.3876
49242 |  |  |  |  | 1 | 1 |  |  | 840 | [6 empty] | 21 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 18 | 0 | 1.8 | 0.01 | 202.08 | 1 | 0.1083
48504 |  |  |  |  | 1 | 0.999 | 1 |  | 0 | [6 empty] | 1095 | 246 | 0 | 23 | 0 | 466 | 2 | 358 | 0 | 0 | 0 | 10.24 | 0.09 | 119.52 | 0.9998 | 0.0829
49403 |  |  |  |  | 1 | 1 | 1 |  | 100 | [6 empty] | 113 | 14 | 0 | 0 | 0 | 0 | 82 | 17 | 0 | 0 | 0 | 15.89 | 0.09 | 175.46 | 0.9996 | 1.5457
49013 |  |  |  |  | 1 | 1 | 1 |  | 137 | [6 empty] | 294 | 0 | 114 | 0 | 0 | 0 | 177 | 0 | 0 | 3 | 0 | 54.65 | 0.32 | 169.34 | 0.9987 | 0.1844
49504 |  |  |  |  | 1 | 0.995 | 1 |  | 13 | [6 empty] | 5142 | 8 | 0 | 36 | 0 | 1 | 2 | 3808 | 71 | 1216 | 0 | 23.28 | 0.27 | 87.35 | 0.9995 | 0.0124
49455 |  |  |  |  | 1 | 0.182 |  |  | 1 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 1 | 0 | 0 | 5.58 | 0.01 | 645.12 | 0.9999 | 0.0087
48622 |  |  |  |  | 1 | 0.997 |  |  | 0 | [6 empty] | 293 | 170 | 20 | 0 | 0 | 0 | 94 | 1 | 0 | 7 | 1 | 10.81 | 0.08 | 130.44 | 0.9997 | 0.2195
48603 |  |  |  |  | 1 | 0.391 | 1 |  | 3 | [6 empty] | 3297 | 2926 | 0 | 358 | 0 | 0 | 0 | 12 | 0 | 1 | 0 | 97.49 | 0.21 | 473.49 | 0.9977 | 0.3879
49676 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 91 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 90 | 0 | 9.74 | 0.05 | 211.46 | 0.9998 | 0.002
49639 |  |  |  |  | 1 | 0.944 |  |  | 0 | [6 empty] | 18 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 2 | 0 | 0 | 8.65 | 0.04 | 206.07 | 0.9998 | 0.0326
49450 |  |  |  |  | 1 | 0.933 | 1 |  | 7 | [6 empty] | 85 | 7 | 0 | 6 | 0 | 0 | 21 | 1 | 0 | 0 | 50 | 5.23 | 0.05 | 113.93 | 0.9999 | 0.8623
48809 |  |  |  |  | 1 | 1 | 1 |  | 216 | [6 empty] | 1398 | 286 | 60 | 443 | 0 | 1 | 2 | 0 | 1 | 604 | 1 | 19.02 | 0.17 | 109.47 | 0.9996 | 0.1137
48656 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.12 | 0 | 128.72 | 1 | 0.0704
48823 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 148 | 1 | 0 | 1 | 0 | 70 | 1 | 0 | 0 | 0 | 75 | 4.84 | 0.01 | 325.78 | 0.9999 | 0.0812
49615 |  |  |  |  | 1 | 0.739 |  |  | 0 | [6 empty] | 311 | 299 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.82 | 0.13 | 452.84 | 0.9986 | 0.0204
48877 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 70 | 69 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 15.73 | 0.09 | 173.08 | 0.9996 | 0.0208
48133 |  |  |  |  | 1 | 0.8 |  |  | 0 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3 | 0 | 0.76 | 0 | 379.99 | 1 | 0.0024
49684 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 262 | 13 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 19.69 | 0.08 | 235.06 | 0.9995 | 1.0412
49657 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 509 | 1 | 196 | 0 | 0 | 0 | 75 | 0 | 0 | 10 | 227 | 36.94 | 0.27 | 136.95 | 0.9991 | 0.1139
49713 |  |  |  |  | 1 | 0.953 |  |  | 0 | [6 empty] | 64 | 1 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 15.09 | 0.1 | 149.68 | 0.9997 | 1.178
48917 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 23 | 1 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 6.23 | 0.04 | 164.94 | 0.9999 | 0.0066
48634 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 39 | 37 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0.02 | 217.91 | 0.9999 | 0.0113
49228 |  |  |  |  | 1 | 1 | 1 |  | 12 | [6 empty] | 2068 | 2050 | 0 | 0 | 0 | 0 | 0 | 13 | 2 | 3 | 0 | 134.62 | 0.86 | 156.56 | 0.9969 | 0.6067
48438 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0 | 350.05 | 1 | 0.1952
49235 |  |  |  |  | 1 | 1 |  |  | 15 | [6 empty] | 54 | 10 | 0 | 0 | 0 | 0 | 36 | 8 | 0 | 0 | 0 | 3.94 | 0.08 | 50.06 | 0.9999
49327 |  |  |  |  | 1 | 1 | 1 |  | 40 | [6 empty] | 160 | 10 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 1 | 0 | 6.78 | 0.04 | 157.52 | 0.9998 | 0.0352
48891 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 39 | 1 | 0.0082
49096 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 69 | 22 | 4 | 0 | 0 | 33 | 0 | 9 | 0 | 0 | 1 | 12.01 | 0.07 | 177.82 | 0.9997 | 0.3386
48532 |  |  |  |  | 1 | 0.991 | 1 |  | 1 | [6 empty] | 115 | 57 | 0 | 2 | 0 | 0 | 8 | 0 | 16 | 1 | 31 | 1.61 | 0.01 | 142.85 | 1 | 1.0131
48750 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 418 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.1 | 0 | 369.5 | 1 | 0.0053
48815 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 8 | 1 | 2 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 2.21 | 0.01 | 300.11 | 0.9999 | 0.244
49287 |  |  |  |  | 1 | 0.32 |  |  | 14 | [6 empty] | 122 | 26 | 1 | 0 | 0 | 0 | 34 | 61 | 0 | 0 | 0 | 64.13 | 0.11 | 596.06 | 0.9985 | 0.4233
49506 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1303 | 42 | 1227 | 0 | 0 | 0 | 1 | 2 | 14 | 0 | 17 | 17.9 | 0.09 | 188.74 | 0.9996 | 0.0777
48631 |  |  |  |  | 1 | 0.3 |  |  | 0 | [6 empty] | 10 | 6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2 | 1.85 | 0 | 458.21 | 1 | 0.0266
48618 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 534 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 199 | 0 | 12.58 | 0.19 | 65.01 | 0.9997 | 0.0196
49329 |  |  |  |  | 1 | 1 | 1 |  | 159 | [6 empty] | 36 | 5 | 1 | 1 | 0 | 1 | 0 | 24 | 0 | 4 | 0 | 2.15 | 0.01 | 186.35 | 1 | 0.7808
49021 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 69 | 32 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 23 | 0 | 2.33 | 0.02 | 100.23 | 0.9999 | 0.1107
48838 |  |  |  |  | 1 | 1 | 1 |  | 446 | [6 empty] | 1058 | 226 | 223 | 3 | 0 | 0 | 115 | 17 | 1 | 450 | 23 | 14.56 | 0.11 | 130.68 | 0.9997 | 0.1298
49233 |  |  |  |  | 1 | 1 |  |  | 14 | [6 empty] | 30 | 17 | 0 | 0 | 0 | 0 | 1 | 0 | 8 | 0 | 4 | 2.23 | 0.02 | 119.06 | 0.9999 | 0.0669
48890 |  |  |  |  | 1 | 0.667 |  |  | 1 | [6 empty] | 3 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.48 | 0 | 432.41 | 1 | 0.0343
49304 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0.74 | 0 | 496.61 | 1 | 0.0015
48414 |  |  |  |  | 1 | 0.5 | 1 |  | 0 | [6 empty] | 12 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2.2 | 0.01 | 204.55 | 0.9999 | 0.0331
48846 |  |  |  |  | 1 | 1 | 1 |  | 36 | [6 empty] | 416 | 1 | 128 | 157 | 0 | 0 | 34 | 80 | 0 | 15 | 1 | 3.63 | 0.03 | 104.04 | 0.9999 | 0.3442
48626 |  |  |  |  | 1 | 0.991 | 1 |  | 0 | [6 empty] | 115 | 67 | 1 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 12 | 8.46 | 0.04 | 203.86 | 0.9998 | 0.1137
49034 |  |  |  |  | 1 | 1 |  |  | 63 | [6 empty] | 28 | 2 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 3.02 | 0.02 | 121.79 | 0.9999 | 0.0284
48636 |  |  |  |  | 1 | 0.392 |  |  | 0 | [6 empty] | 102 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 1 | 0 | 56.63 | 0.13 | 435.25 | 0.9987 | 0.0026
49630 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 220 | 0 | 0 | 1 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 35.52 | 0.16 | 223.51 | 0.9992 | 0.0951
49083 |  |  |  |  | 1 | 1 |  |  | 227 | [6 empty] | 228 | 22 | 0 | 0 | 0 | 152 | 52 | 2 | 0 | 0 | 0 | 14.2 | 0.05 | 260.92 | 0.9997 | 0.0143
49436 | [8 empty] | 0
49740 | [30 empty] | 0.0206
49087 | [8 empty] | 0 | [21 empty] | 0.0056
49655 | [8 empty] | 0 | [21 empty] | 0.0019
49682 | [8 empty] | 0 | [21 empty] | 0.1372
49336 | [8 empty] | 0 | [21 empty] | 0.7869
48464 | [8 empty] | 0
48893 | [8 empty] | 0 | [21 empty] | 0.0806
48157 | [8 empty] | 0 | [21 empty] | 0.0013
49701 | [8 empty] | 0 | [21 empty] | 0.0093
48738 | [8 empty] | 0 | [21 empty] | 0.4695
48348
48350 | [8 empty] | 0 | [21 empty] | 0.0019
49791 | [30 empty] | 0.4011
48853
48446 | [8 empty] | 0
49340 | [8 empty] | 0 | [21 empty] | 0.0034
49440 | [8 empty] | 0 | [21 empty] | 0.0009
48140 | [8 empty] | 0
49505 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 72 | 26 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 24 | 0.68 | 0 | 141.26 | 1 | 0.0713
48883 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 440 | 2 | 0 | 0 | 0 | 0 | 22 | 0 | 12 | 148 | 256 | 12.7 | 0.16 | 80.21 | 0.9997 | 0.0828
48617 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 150 | 114 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 24 | 0 | 3.72 | 0.03 | 115.9 | 0.9999 | 0.0452
48647 |  |  |  |  | 1 | 0.242 | 1 |  | 0 | [6 empty] | 126 | 18 | 1 | 0 | 0 | 0 | 104 | 0 | 1 | 2 | 0 | 13.65 | 0.03 | 427.8 | 0.9997 | 0.0013
49415 |  |  |  |  | 1 | 0.998 | 1 |  | 0 | [6 empty] | 676 | 9 | 0 | 0 | 0 | 0 | 662 | 0 | 3 | 1 | 1 | 24.05 | 0.23 | 106.42 | 0.9994 | 0.104
49460 |  |  |  |  | 1 | 0.833 |  |  | 0 | [6 empty] | 6 | 0 | 1 | 0 | 0 | 0 | 3 | 1 | 0 | 1 | 0 | 0.37 | 0 | 276.81 | 1 | 0.1455
48732 |  |  |  |  | 1 | 0.853 | 1 |  | 46 | [6 empty] | 321 | 225 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 47 | 47 | 8.65 | 0.06 | 155.8 | 0.9998 | 0.2706
49284 |  |  |  |  | 1 | 0.07 | 1 |  | 1 | [6 empty] | 1274 | 1034 | 0 | 0 | 0 | 8 | 0 | 208 | 0 | 24 | 0 | 721.99 | 0.71 | 1021.22 | 0.9833 | 0.0721
48756 |  |  |  |  | 1 | 0.974 | 1 |  | 0 | [6 empty] | 74 | 1 | 71 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2.19 | 0.02 | 102.11 | 0.9999 | 0.8039
49412 |  |  |  |  | 1 | 0.994 |  |  | 8 | [6 empty] | 188 | 63 | 1 | 8 | 0 | 0 | 107 | 1 | 6 | 1 | 1 | 1.38 | 0.03 | 45.13 | 1 | 0.0966
49456 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 64 | 16 | 0 | 0 | 0 | 0 | 38 | 0 | 8 | 2 | 0 | 1.86 | 0.01 | 209.23 | 1 | 0.0074
49328 |  |  |  |  | 1 | 0.95 | 1 |  | 0 | [6 empty] | 40 | 2 | 3 | 0 | 0 | 0 | 34 | 1 | 0 | 0 | 0 | 9.89 | 0.02 | 423.99 | 0.9998 | 0.3289
49654 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.45 | 0 | 209.67 | 1 | 0.0011
49668 |  |  |  |  | 1 | 1 |  |  | 272 | [6 empty] | 194 | 0 | 0 | 1 | 0 | 0 | 132 | 0 | 0 | 0 | 61 | 7.24 | 0.08 | 93.98 | 0.9998 | 0.4521
49325 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 31 | 1 | 0 | 0 | 0 | 18 | 11 | 0 | 0 | 1 | 0 | 7.33 | 0.04 | 201.5 | 0.9998 | 0.0211
49677 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 400 | 1 | 0 | 1 | 0 | 0 | 0 | 215 | 0 | 183 | 0 | 33.62 | 0.2 | 167.02 | 0.9992 | 0.0515
48658 |  |  |  |  | 1 | 0.143 | 1 |  | 9 | [6 empty] | 8 | 1 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.17 | 0 | 450.68 | 1 | 0.022
49338 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 38 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 9.36 | 0.07 | 126.07 | 0.9998 | 0.0742
49229 |  |  |  |  | 1 | 1 |  |  | 662 | [6 empty] | 450 | 6 | 0 | 442 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.98 | 0.01 | 152.71 | 1 | 0.0894
49799 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 113 | 11.48 | 0.2 | 58.14 | 0.9997 | 0.0319
49632 |  |  |  |  | 1 | 0.333 |  |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1.59 | 0 | 498.57 | 1 | 0.0682
49002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 16 | 12 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0.15 | 0 | 100.04 | 1 | 0.0246
49088 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 55 | 1 | 0.0179
48742 |  |  |  |  | 1 | 0.999 | 1 |  | 4 | [6 empty] | 2279 | 44 | 1 | 0 | 778 | 0 | 1416 | 0 | 0 | 39 | 1 | 129.31 | 0.9 | 143.18 | 0.997 | 0.7768
49058 |  |  |  |  | 1 | 1 | 1 |  | 32 | [6 empty] | 261 | 151 | 1 | 37 | 0 | 0 | 1 | 1 | 65 | 0 | 5 | 2.99 | 0.03 | 116.15 | 0.9999 | 0.0476
49616 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 90 | 0 | 0 | 0 | 0 | 0 | 55 | 35 | 0 | 0 | 0 | 7.71 | 0.06 | 125.88 | 0.9998 | 0.0585
48860 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.2 | 0 | 63.95 | 1 | 0.0403
49286 |  |  |  |  | 1 | 0.75 |  |  | 294 | [6 empty] | 529 | 246 | 1 | 0 | 0 | 0 | 231 | 33 | 0 | 18 | 0 | 23.17 | 0.09 | 264.22 | 0.9995 | 0.3216
49441 |  |  |  |  | 1 | 0.995 |  |  | 0 | [6 empty] | 1218 | 107 | 0 | 1000 | 0 | 0 | 66 | 1 | 29 | 13 | 2 | 1.27 | 0.01 | 109.31 | 1 | 0.003
49716 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 10.21 | 0.03 | 387.16 | 0.9998 | 0.1142
49007 |  |  |  |  | 1 | 0.984 | 1 |  | 1 | [6 empty] | 748 | 0 | 0 | 0 | 0 | 0 | 24 | 724 | 0 | 0 | 0 | 21.32 | 0.12 | 176.89 | 0.9995 | 0.0113
48439 |  |  |  |  | 1 | 0.999 | 1 |  | 3 | [6 empty] | 837 | 608 | 0 | 31 | 0 | 0 | 36 | 0 | 1 | 0 | 161 | 5.94 | 0.03 | 178.92 | 0.9999 | 0.0147
49779 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 117 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.51 | 0.06 | 164.77 | 0.9998 | 0.001
49435 |  |  |  |  | 1 | 1 | 1 |  | 34 | [6 empty] | 248 | 4 | 0 | 77 | 0 | 143 | 14 | 7 | 3 | 0 | 0 | 14.33 | 0.1 | 146.16 | 0.9997 | 0.0591
49076 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 503 | 145 | 169 | 0 | 0 | 64 | 0 | 88 | 0 | 37 | 0 | 29.46 | 0.28 | 106.48 | 0.9993 | 0.0231
49405 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 1.53 | 0.01 | 120.62 | 1 | 0.0127
48878 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 85 | 1 | 0.0013
49068 |  |  |  |  | 1 | 1 | 1 |  | 459 | [6 empty] | 45 | 15 | 0 | 0 | 0 | 25 | 1 | 0 | 3 | 1 | 0 | 2.47 | 0.01 | 178.29 | 0.9999 | 0.1002
49770 |  |  |  |  | 1 | 0.679 |  |  | 0 | [6 empty] | 240 | 0 | 0 | 0 | 0 | 79 | 161 | 0 | 0 | 0 | 0 | 40.94 | 0.16 | 253.98 | 0.9991 | 0.1377
49078 |  |  |  |  | 1 | 1 | 1 |  | 32 | [6 empty] | 522 | 2 | 1 | 0 | 0 | 0 | 367 | 106 | 0 | 46 | 0 | 20.7 | 0.13 | 163.86 | 0.9995 | 0.1607
49424 |  |  |  |  | 1 | 0.994 | 1 |  | 0 | [6 empty] | 182 | 25 | 0 | 0 | 0 | 0 | 155 | 0 | 1 | 1 | 0 | 2.67 | 0.02 | 135.51 | 0.9999 | 0.0081
49618 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2.14 | 0.01 | 225 | 1 | 0.2405
49236 |  |  |  |  | 1 | 0.045 | 1 |  | 52 | [6 empty] | 155 | 0 | 0 | 0 | 0 | 0 | 109 | 1 | 0 | 45 | 0 | 230.74 | 0.57 | 403.42 | 0.9947 | 3.9077
49234 |  |  |  |  | 1 | 0.966 |  |  | 44 | [6 empty] | 58 | 12 | 0 | 0 | 0 | 0 | 43 | 0 | 1 | 2 | 0 | 2.78 | 0.03 | 84.85 | 0.9999 | 0.1762
48625 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 683 | 307 | 0 | 0 | 0 | 0 | 305 | 1 | 0 | 0 | 70 | 7.26 | 0.06 | 129.1 | 0.9998 | 0.1041
48505 |  |  |  |  | 1 | 0.978 | 1 |  | 0 | [6 empty] | 156 | 14 | 0 | 45 | 0 | 38 | 0 | 17 | 0 | 40 | 2 | 2.91 | 0.01 | 231 | 0.9999 | 0.0507
49307 |  |  |  |  | 1 | 0.994 | 1 |  | 0 | [6 empty] | 200 | 10 | 0 | 0 | 0 | 0 | 177 | 1 | 11 | 1 | 0 | 2.74 | 0.03 | 106.77 | 0.9999 | 0.0916
48615 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 33 | 15 | 1 | 0 | 0 | 0 | 2 | 0 | 9 | 6 | 0 | 2.45 | 0.02 | 111.55 | 0.9999 | 0.1164
48635 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 695 | 1 | 5 | 0 | 0 | 0 | 689 | 0 | 0 | 0 | 0 | 33.57 | 0.31 | 107.91 | 0.9992 | 1.355
49426 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 381 | 254 | 2 | 35 | 0 | 1 | 84 | 1 | 1 | 3 | 0 | 2.05 | 0.02 | 96.36 | 1 | 0.0383
49613 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 36 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 32 | 0 | 3.96 | 0.04 | 97.75 | 0.9999 | 0.1329
48906 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 42 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.43 | 0.01 | 126.03 | 1 | 0.198
49421 |  |  |  |  | 1 | 1 | 1 |  | 52 | [6 empty] | 1193 | 456 | 13 | 0 | 0 | 1 | 721 | 1 | 0 | 1 | 0 | 27.93 | 0.6 | 46.81 | 0.9994 | 0.4422
48529 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 142 | 126 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 6 | 4.35 | 0.03 | 156.69 | 0.9999 | 0.1391
49259 |  |  |  |  | 1 | 1 | 1 |  | 112 | [6 empty] | 51 | 26 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 22 | 0 | 4.8 | 0.04 | 133.3 | 0.9999 | 0.0812
48652 |  |  |  |  | 1 | 0 |  |  | 4 | [6 empty] | 8 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 2.92 | 0 | 624.34 | 0.9999 | 0.0433
48888 |  |  |  |  | 1 | 1 | 1 |  | 23 | [6 empty] | 48 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 2.71 | 0.02 | 177.29 | 0.9999 | 0.0702
48747 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.06 | 0 | 53.35 | 1 | 0.0266
48415 |  |  |  |  | 1 | 0.563 | 1 |  | 0 | [6 empty] | 20 | 15 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.43 | 0 | 324.82 | 1 | 0.0276
49631 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 50 | 4 | 1 | 0 | 0 | 0 | 44 | 0 | 1 | 0 | 0 | 3.78 | 0.02 | 164.99 | 0.9999 | 0.1874
49315 |  |  |  |  | 1 | 0.999 | 0.978 |  | 0 | [6 empty] | 1798 | 281 | 1 | 81 | 0 | 0 | 205 | 1183 | 2 | 40 | 5 | 26.43 | 0.15 | 180.38 | 0.9994 | 0.1811
48845 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.12 | 0 | 367 | 1 | 0.1555
48832 |  |  |  |  | 1 | 0.991 | 1 |  | 0 | [6 empty] | 113 | 74 | 1 | 0 | 0 | 0 | 37 | 0 | 1 | 0 | 0 | 25.06 | 0.17 | 149.71 | 0.9994 | 0.1333
49448 |  |  |  |  | 1 | 1 | 1 |  | 17 | [6 empty] | 19 | 2 | 1 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 2.25 | 0.01 | 229.75 | 0.9999 | 0.0314
48417 |  |  |  |  | 1 | 0.667 | 1 |  | 1 | [6 empty] | 4 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1.74 | 0 | 556.89 | 1 | 1.5975
48473 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 193 | 3 | 41 | 10 | 0 | 0 | 52 | 0 | 0 | 86 | 1 | 3.56 | 0.02 | 198.29 | 0.9999 | 0.0097
48657 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 4 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0.26 | 0 | 266.25 | 1 | 0.0294
49645 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 2.37 | 0.04 | 59.53 | 0.9999 | 0.0112
49241 |  |  |  |  | 1 | 0.98 |  |  | 167 | [6 empty] | 50 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 39 | 0 | 7.59 | 0.04 | 171.22 | 0.9998 | 0.0807
49220 |  |  |  |  | 1 | 0.997 |  |  | 154 | [6 empty] | 732 | 4 | 0 | 0 | 0 | 0 | 53 | 0 | 610 | 7 | 58 | 88.36 | 0.67 | 132.66 | 0.998 | 0.4741
48808 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 123 | 1 | 88 | 1 | 0 | 32 | 0 | 0 | 0 | 1 | 0 | 5.83 | 0.05 | 127.77 | 0.9999 | 0.0531
49009 |  |  |  |  | 1 | 0.969 | 1 |  | 2168 | [6 empty] | 742 | 54 | 1 | 66 | 0 | 112 | 323 | 84 | 3 | 36 | 63 | 3.38 | 0.03 | 115.12 | 0.9999 | 0.1462
48766 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 160.03 | 1 | 0.0518
49348 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 26 | 13 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 12 | 0 | 0.84 | 0 | 184.29 | 1 | 0.0617
48835 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 0 | 211 | 1 | 0.0195
48821 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 9 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37 | 0 | 118.81 | 1 | 0.0018
49052 |  |  |  |  | 1 | 1 |  |  | 19 | [6 empty] | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.85 | 0.04 | 108.15 | 0.9999 | 0.0022
49090 |  |  |  |  | 1 | 1 | 1 |  | 89 | [6 empty] | 858 | 1 | 211 | 280 | 0 | 1 | 365 | 0 | 0 | 0 | 0 | 51.56 | 0.25 | 206.53 | 0.9988 | 0.5309
48503 |  |  |  |  | 1 | 0.949 |  |  | 0 | [6 empty] | 1391 | 691 | 0 | 28 | 0 | 605 | 3 | 0 | 0 | 1 | 63 | 14.34 | 0.11 | 126.1 | 0.9997 | 0.2233
49201 |  |  |  |  | 1 | 0.992 | 1 |  | 482 | [6 empty] | 422 | 88 | 0 | 25 | 0 | 2 | 186 | 88 | 2 | 25 | 6 | 3.88 | 0.02 | 198.52 | 0.9999 | 0.1274
48458 |  |  |  |  | 1 | 0.995 | 1 |  | 40 | [6 empty] | 245 | 222 | 0 | 1 | 0 | 2 | 1 | 18 | 0 | 0 | 1 | 3.35 | 0.03 | 131.61 | 0.9999 | 0.0084
49620 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 22 | 13 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 3.2 | 0.02 | 162.01 | 0.9999 | 0.0126
49010 |  |  |  |  | 1 | 0.763 | 1 |  | 0 | [6 empty] | 345 | 3 | 22 | 0 | 0 | 0 | 238 | 46 | 2 | 34 | 0 | 13.86 | 0.04 | 353.35 | 0.9997 | 0.4878
49267 |  |  |  |  | 1 | 0.998 |  |  | 14 | [6 empty] | 569 | 374 | 0 | 0 | 0 | 0 | 3 | 186 | 0 | 6 | 0 | 73.92 | 0.26 | 279.05 | 0.9983 | 0.6979
48801 |  |  |  |  | 1 | 1 |  |  | 6 | [6 empty] | 28 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0.29 | 0 | 60.25 | 1 | 0.0043
49503 |  |  |  |  | 1 | 0.971 | 1 |  | 0 | [6 empty] | 2319 | 173 | 67 | 0 | 0 | 0 | 1745 | 205 | 49 | 75 | 5 | 15.26 | 0.11 | 137.89 | 0.9996 | 0.1883
49302 |  |  |  |  | 1 | 0.993 | 1 |  | 0 | [6 empty] | 151 | 83 | 2 | 0 | 0 | 41 | 1 | 1 | 22 | 1 | 0 | 3.83 | 0.04 | 91 | 0.9999 | 0.2478
49675 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.14 | 0 | 83.97 | 1 | 0.0008
49747 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1050 | 1 | 1 | 0 | 1047 | 0 | 0 | 0 | 0 | 0 | 1 | 0.83 | 0 | 298.63 | 1 | 0.0381
48430 |  |  |  |  | 1 | 0.882 | 1 |  | 12 | [6 empty] | 186 | 111 | 0 | 6 | 0 | 37 | 0 | 0 | 28 | 1 | 3 | 1.75 | 0.01 | 183.42 | 1 | 0.0417
49638 |  |  |  |  | 1 | 1 |  |  | 82 | [6 empty] | 365 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 50.28 | 0.48 | 104.69 | 0.9988 | 1.4829
49203 |  |  |  |  | 1 | 1 |  |  | 105 | [6 empty] | 324 | 34 | 0 | 52 | 0 | 0 | 53 | 0 | 168 | 17 | 0 | 1.93 | 0.02 | 126.1 | 1 | 0.0794
49646 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2 | 0 | 0 | 0.37 | 0 | 129.59 | 1 | 0.1912
49250 |  |  |  |  | 1 | 0.975 |  |  | 652 | [6 empty] | 40 | 2 | 0 | 0 | 0 | 0 | 23 | 1 | 0 | 11 | 3 | 1.15 | 0.01 | 87.94 | 1 | 0.0857
48856 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5.28 | 0.05 | 113.54 | 0.9999 | 0.0129
48604 |  |  |  |  | 1 | 0.939 | 0.833 |  | 0 | [6 empty] | 39 | 1 | 1 | 0 | 0 | 0 | 0 | 4 | 4 | 28 | 1 | 2 | 0.01 | 286.23 | 1 | 1.1436
Zip Group 1 |  |  |  |  | 1 | 0.895 | 1 |  | 297 | [6 empty] | 1554 | 336 | 69 | 185 | 33 | 91 | 421 | 156 | 24 | 153 | 86 | 2528.96 | 13.23 | 191.19 | 0.9415 | 26.4158
48881 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 35 | 6 | 28 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1.53 | 0.01 | 108.62 | 1 | 0.0307
48745 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 388 | 0 | 174 | 1 | 2 | 131 | 69 | 11 | 0 | 0 | 0 | 74.28 | 0.38 | 197.38 | 0.9983 | 0.6364
48739 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 916 | 2 | 240 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 637 | 41.35 | 0.19 | 216.78 | 0.999 | 0.3007
48640 |  |  |  |  | 1 | 1 | 1 |  | 20 | [6 empty] | 2058 | 119 | 1 | 1 | 0 | 1055 | 539 | 4 | 0 | 314 | 25 | 14.09 | 0.13 | 105.85 | 0.9997 | 0.2865
49512 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 33 | 3 | 0 | 1 | 0 | 0 | 0 | 26 | 0 | 0 | 3 | 0.39 | 0 | 133.09 | 1 | 0.0044
48854 |  |  |  |  | 1 | 1 |  |  | 663 | [6 empty] | 156 | 3 | 0 | 3 | 0 | 0 | 1 | 0 | 149 | 0 | 0 | 1.76 | 0.02 | 101.55 | 1 | 0.0981
49252 |  |  |  |  | 1 | 1 | 1 |  | 309 | [6 empty] | 505 | 0 | 0 | 0 | 0 | 15 | 343 | 2 | 0 | 145 | 0 | 32.41 | 0.35 | 91.64 | 0.9992 | 0.0539
49004 |  |  |  |  | 1 | 1 | 1 |  | 155 | [6 empty] | 58 | 20 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 34 | 1 | 0.84 | 0.01 | 112.8 | 1 | 0.0188
49601 |  |  |  |  | 1 | 1 | 1 |  | 12 | [6 empty] | 678 | 1 | 110 | 0 | 0 | 219 | 141 | 38 | 166 | 0 | 3 | 4.81 | 0.06 | 86.66 | 0.9999 | 0.0931
49548 |  |  |  |  | 1 | 0.999 |  |  | 0 | [6 empty] | 2014 | 0 | 0 | 163 | 0 | 0 | 0 | 794 | 8 | 1049 | 0 | 16.75 | 0.12 | 135.97 | 0.9996 | 0.2032
49318 |  |  |  |  | 1 | 1 | 1 |  | 130 | [6 empty] | 33 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 1 | 0 | 0 | 7.81 | 0.04 | 183.63 | 0.9998 | 0.0206
49519 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1688 | 60 | 0 | 0 | 0 | 1358 | 0 | 0 | 13 | 257 | 0 | 14.64 | 0.13 | 113.1 | 0.9997 | 0.0583
48437
48862 | [8 empty] | 0 | [21 empty] | 0.1304
48462 | [8 empty] | 0
49718 | [8 empty] | 0
48502 | [8 empty] | 0 | [21 empty] | 0.001
49045 | [8 empty] | 0 | [21 empty] | 0.3182
49227 | [8 empty] | 100 | [21 empty] | 0.0028
49097 | [8 empty] | 16 | [21 empty] | 0.13
49305 | [8 empty] | 0 | [21 empty] | 0.0239
48421 | [8 empty] | 0
49035 | [30 empty] | 1.4706
49446 | [8 empty] | 0 | [21 empty] | 0.0046
49029 | [8 empty] | 3 | [21 empty] | 0.3374
49730 | [30 empty] | 1.6239
48613 | [8 empty] | 11
48630 | [8 empty] | 0 | [21 empty] | 0.0146
49625 | [30 empty] | 0.1875
MPSC Annual Performance Standard | 95% or more | 90% or more completed within 15 business days | 90% or more within 120 minutes in MSAs | 90% or more within 180 minutes in non-MSAs | 90% or more customers restored in 36 hours or less | 90% or more customers restored in 8 hours or less | 90% or more customers restored in 24 hours or less | 90% or more customers restored in 48 hours or less | 6% or less before 2030; 5% or less in 2030 or later

## Census Tract
RELIABILITY DATA TEMPLATE
Utility: | Consumers Energy Co. |  |  | □ Required Fields
Reporting Month: | 2023-04-30 |  |  | ■ Optional Fields
Census Tract Year: | 2010-01-01
RELIABILITY DATA REPORTED BY CENSUS TRACT
| Meter Reading Factor R460.732 (a) | New Service Installation Factor R460.732(b) | Wire Down Relief Factor R460.732 (c) |  | Outage Restoration |  |  |  | CEMI4 | Line Clearing/ Tree Trimming | [5 empty] | Total Customer outages | Outage Causes | [9 empty] | Reliability Metrics (all weather)
[5 empty] | All Conditions R460.732 (d) | Normal Conditions R460.732 (e) | Gray-Sky Conditions R460.732 (f) | Catastrophic Conditions R460.732 (g) | Sustained Interruptions R460.732 (h(i)) | [7 empty] | Equipment | Lightning | Planned | Power Supply | Public | Vegetation | Weather (other than lightning) | Wildlife | Unknown | Other | SAIDI | SAIFI | CAIDI | ASAI | MAIFI
Census Tract Number | Meter Reading Factor (Percentage) | New Services Installed in 15 Business Days or Less (Percentage) | The percentage of the first responder guarded downed wires that are relieved by an electric utility representative within 120 minutes after notification in MSAs. | The percentage of the first responder guarded downed wires that are relieved by an electric utility representative within 180 minutes after notification in non-MSAs. | Percentage of Customers Restored in 36 Hours or Less | Percentage of Customers Restored in 8 Hours or Less | Percentage of Customers Restored in 24 Hours or Less | Percentage of Customers Restored in 48 Hours or Less | Number of Customers Experiencing 4 or More Sustained Interruptions | Amount of Line Cleared (miles) | Capital Spend ($) | O&M Spend ($) | Quarterly Line Clearing Target (miles) | Quarterly Line Clearing Target (% of internal target met) | Cumulative Line Clearing Target (%) | Total Customer outages | Total number of outages causes by equipment failure | Total number of outages caused by lightning | Total number of planned and forced outages | Total number of outages caused by transmission or generation failure | Total number of outages caused by an act of the public at large | Total number of outages caused by trees | Total number of outages caused by wind, snow, ice, hail, and rain | Total number of outages caued by animal interference | Total number of outages caused by unknonwn causes | Total number of outages caused by other causes | System Average Interruption Duration Index | System Average Interruption Frequency Index | Customer Average Interruption Duration Index (contribution to total CAIDI) | Average Service Availability Index | Momentary Average Interruption Frequency Index
26145012900 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 66 | 4 | 0 | 0 | 0 | 0 | 61 | 1 | 0 | 0 | 0 | 3.46 | 0.03 | 111.9 | 0.9999 | 0.9738
26159010900 |  |  |  |  | 1 | 1 | 1 |  | 38 | [6 empty] | 378 | 5 | 0 | 0 | 0 | 0 | 47 | 326 | 0 | 0 | 0 | 24.04 | 0.21 | 116.89 | 0.9994 | 0.5413
26023951000 |  |  |  |  | 1 | 1 |  |  | 480 | [6 empty] | 2285 | 1 | 0 | 2178 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 4.88 | 0.05 | 102.2 | 0.9999 | 0.2621
26049011601 |  |  |  |  | 1 | 0.553 |  |  | 0 | [6 empty] | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 2 | 0 | 16.97 | 0.03 | 550.53 | 0.9996 | 0.2028
26081013600 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.69 | 0 | 651 | 1 | 0.0011
26049012602 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0.01 | 395.68 | 0.9999
26121000100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.27 | 0 | 325.32 | 1 | 0.058
26049012003 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 106.69 | 1 | 0.0007
26077001702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.08 | 0 | 82.08 | 1 | 0.002
26145001700 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.15 | 0 | 143.38 | 1 | 1.3491
26081011803 | [8 empty] | 0 | [21 empty] | 0.0028
26087342000 | [8 empty] | 0 | [21 empty] | 0.0625
26081004100 | [8 empty] | 0 | [21 empty] | 0.6228
26077002802 | [8 empty] | 100 | [21 empty] | 0.0392
26121000601 | [30 empty] | 0.0026
26081002800 | [8 empty] | 0 | [21 empty] | 0.3099
26093711000 | [8 empty] | 0 | [21 empty] | 0.0682
26029001200 | [30 empty] | 0.4519
26081014000 | [8 empty] | 0 | [21 empty] | 0.0004
26141950100 | [8 empty] | 0
26049012702 | [8 empty] | 0 | [6 empty] | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0066
26077001604 | [8 empty] | 25 | [21 empty] | 0.0009
26049010501 | [8 empty] | 0 | [21 empty] | 0.166
26139020503 | [8 empty] | 0 | [21 empty] | 0.0009
26049011610 | [8 empty] | 0 | [21 empty] | 0.0433
26081001101 | [8 empty] | 0 | [21 empty] | 0.0085
26049010113 | [8 empty] | 0 | [21 empty] | 0.0155
26017285800 | [8 empty] | 0 | [21 empty] | 0.0014
26025000700 | [8 empty] | 0 | [21 empty] | 0.0094
26121000500 | [8 empty] | 0 | [21 empty] | 0.001
26145012001 | [8 empty] | 0 | [21 empty] | 0.5149
26101000800 | [8 empty] | 0 | [21 empty] | 0.0053
26077006601 | [8 empty] | 0 | [21 empty] | 0.2936
26055551500 | [30 empty] | 1.2588
26091061600 | [8 empty] | 0 | [21 empty] | 0.0032
26037010203
26125126300 | [30 empty] | 0.0034
26137950600 | [8 empty] | 0 | [21 empty] | 0.0038
26047970400 | [30 empty] | 0.0094
26077006103 | [8 empty] | 0
26067030200 | [8 empty] | 0 | [21 empty] | 0.0154
26075006303 | [8 empty] | 9 | [21 empty] | 0.0046
26081003100 | [8 empty] | 0 | [21 empty] | 0.9845
26049012201 | [8 empty] | 0 | [21 empty] | 0.0048
26155030700 | [8 empty] | 0 | [21 empty] | 0.6874
26065006301 | [8 empty] | 3 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0088
26049011508 | [8 empty] | 0 | [21 empty] | 0.2204
26045021302 | [30 empty] | 0.4286
26081013000 | [8 empty] | 0 | [21 empty] | 0.0069
26159011900 | [8 empty] | 0
26081011406
26145011600 | [8 empty] | 0 | [21 empty] | 0.0031
26067030300 | [8 empty] | 0 | [21 empty] | 0.0033
26081003800 | [8 empty] | 0 | [21 empty] | 0.3457
26125125600 | [8 empty] | 0
26145000200 | [8 empty] | 0 | [21 empty] | 0.198
26069000400 | [8 empty] | 0 | [21 empty] | 0.0022
26065003902
26077000202 | [8 empty] | 0
26145000700 | [8 empty] | 0 | [21 empty] | 0.484
26121000401 | [8 empty] | 0 | [21 empty] | 0.0483
26049012007 | [8 empty] | 0
26145011500 | [8 empty] | 0 | [6 empty] | 88 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0039
26075000100 | [8 empty] | 1 | [21 empty] | 0.0013
26111290700 | [8 empty] | 0 | [21 empty] | 0.9899
26049011213 | [8 empty] | 0 | [21 empty] | 0.0017
26049013202 | [8 empty] | 0 | [6 empty] | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0019
26025002500 | [8 empty] | 0 | [21 empty] | 0.6527
26049001700 | [8 empty] | 0 | [21 empty] | 0.004
26073940400 | [8 empty] | 0 | [21 empty] | 0.0016
26037010108 | [8 empty] | 0 | [21 empty] | 0.962
26077001507 | [8 empty] | 0 | [21 empty] | 0.2316
26049980100
26087342100 | [8 empty] | 0
26029001300 | [8 empty] | 0 | [21 empty] | 0.0068
26065004403
26081012607 | [8 empty] | 0 | [21 empty] | 0.0006
26045021301 | [8 empty] | 0
26049980000 | [8 empty] | 0
26081002400 | [8 empty] | 0 | [21 empty] | 0.0008
26049000200 | [8 empty] | 0 | [21 empty] | 0.005
26139021801 | [8 empty] | 0 | [21 empty] | 0.0005
26075000600 | [8 empty] | 1 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0375
26075000800 | [8 empty] | 16 | [21 empty] | 0.0321
26049011214 | [8 empty] | 0 | [21 empty] | 0.0004
26055551400 | [8 empty] | 0 | [21 empty] | 0.9802
26025003900 | [8 empty] | 17
26081010402 | [8 empty] | 0 | [21 empty] | 0.0129
26075000500 | [8 empty] | 1
26107960100 | [8 empty] | 0 | [21 empty] | 0.0105
26017285500 | [8 empty] | 0 | [21 empty] | 0.0005
26093710500 | [8 empty] | 0 | [21 empty] | 0.0036
26009960300 | [8 empty] | 0 | [21 empty] | 0.0162
26139023500 | [8 empty] | 0 | [21 empty] | 0.0017
26081012606 | [8 empty] | 0 | [21 empty] | 0.0016
26017285400 | [8 empty] | 0 | [21 empty] | 0.3024
26037011200
26023950200 | [8 empty] | 1 | [21 empty] | 0.1417
26075001300 | [8 empty] | 0 | [21 empty] | 0.0027
26049010110 | [8 empty] | 0 | [21 empty] | 0.0007
26077003302 | [8 empty] | 0 | [21 empty] | 0.0593
26025000900 | [8 empty] | 1 | [21 empty] | 0.6675
26067032100 | [8 empty] | 0 | [21 empty] | 0.0904
26065005304 | [8 empty] | 0
26025001400 | [8 empty] | 7 | [21 empty] | 0.014
26121000300 | [8 empty] | 0 | [21 empty] | 0.0007
26049012906 | [8 empty] | 0
26075006900 | [8 empty] | 16 | [21 empty] | 0.0247
26077002201 | [8 empty] | 36 | [21 empty] | 0.0018
26047970100 | [8 empty] | 0 | [21 empty] | 0.0055
26049003400 | [8 empty] | 0 | [21 empty] | 0.0069
26077001504 | [8 empty] | 1
26047970800 | [30 empty] | 0.1719
26081001300 | [8 empty] | 0 | [21 empty] | 0.3003
26045020403 | [8 empty] | 0 | [21 empty] | 0.0007
26029000900 | [8 empty] | 0 | [21 empty] | 0.0056
26149040900 | [8 empty] | 0 | [21 empty] | 0.0041
26081004600 | [8 empty] | 0 | [21 empty] | 0.0227
26077001603 | [8 empty] | 5 | [21 empty] | 0.0011
26065006302 | [8 empty] | 46 | [21 empty] | 0.021
26035000100 | [8 empty] | 0 | [21 empty] | 0.0048
26049010700 | [8 empty] | 0 | [21 empty] | 0.2295
26055550101 | [8 empty] | 0 | [6 empty] | 201 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.5258
26107960600 | [8 empty] | 0 | [21 empty] | 0.0218
26075000200 | [8 empty] | 1 | [21 empty] | 0.003
26115831000 | [8 empty] | 0
26049001900 | [8 empty] | 0 | [6 empty] | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0043
26075005600 | [8 empty] | 11 | [21 empty] | 0.3814
26005030500 | [8 empty] | 0 | [21 empty] | 0.0028
26065004301 | [30 empty] | 0.0075
26049010201 | [30 empty] | 0.0116
26077001905 | [8 empty] | 0 | [21 empty] | 0.0013
26125123100 | [8 empty] | 0
26069000300 | [8 empty] | 0 | [21 empty] | 0.0028
26145010302 | [8 empty] | 0 | [21 empty] | 0.0029
26077002005 | [8 empty] | 0
26049001800 | [30 empty] | 0.0153
26049000600 | [8 empty] | 0 | [21 empty] | 0.1451
26049011402 | [8 empty] | 0
26025000800 | [8 empty] | 0 | [21 empty] | 0.0393
26081000200 | [8 empty] | 0 | [21 empty] | 0.3299
26081013100 | [8 empty] | 0 | [21 empty] | 0.0019
26107961000 | [8 empty] | 2 | [21 empty] | 0.0593
26049013113 | [8 empty] | 0 | [6 empty] | 53 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0015
26139025100 | [8 empty] | 0 | [21 empty] | 0.003
26157001300 | [8 empty] | 0
26055550400 | [30 empty] | 0.1755
26065004600 | [8 empty] | 0 | [21 empty] | 0.1687
26077001907 | [8 empty] | 2 | [21 empty] | 0.0017
26081014300 | [8 empty] | 0 | [21 empty] | 0.1005
26049012311 | [8 empty] | 0 | [21 empty] | 0.0023
26049001100 | [8 empty] | 0 | [21 empty] | 0.0337
26055551200 | [30 empty] | 0.8696
26077002102 | [8 empty] | 0 | [21 empty] | 0.1499
26045020202
26049011713 | [8 empty] | 0 | [21 empty] | 0.0008
26049003800 | [8 empty] | 0 | [21 empty] | 0.0017
26141950300
26025001200 | [8 empty] | 0 | [21 empty] | 0.97
26111290800 | [8 empty] | 0 | [21 empty] | 0.9755
26073940500 | [8 empty] | 0 | [21 empty] | 0.0062
26077001601 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0015
26127010400 | [8 empty] | 0 | [21 empty] | 0.3504
26077001802 | [8 empty] | 0 | [21 empty] | 0.1165
26139021201 | [8 empty] | 0 | [21 empty] | 0.0007
26009960100 | [8 empty] | 0
26139023600 | [8 empty] | 0
26081002900 | [8 empty] | 0 | [21 empty] | 0.9666
26049012402 | [8 empty] | 0 | [21 empty] | 0.0015
26065005302 | [8 empty] | 0 | [21 empty] | 0.1884
26155030500 | [8 empty] | 0 | [21 empty] | 0.0459
26077006102 | [8 empty] | 0 | [21 empty] | 0.0037
26081014100 | [8 empty] | 0
26045020402 | [8 empty] | 0 | [21 empty] | 0.0012
26065005100
26081003000 | [30 empty] | 0.626
26125126200
26155031800 | [8 empty] | 0 | [6 empty] | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0767
26031960400 | [8 empty] | 0
26049011901 | [8 empty] | 0
26047970700
26081004300 | [8 empty] | 0 | [21 empty] | 0.0011
26047970300 | [30 empty] | 0.0455
26049010810 | [8 empty] | 0 | [21 empty] | 0.0009
26155030800 | [30 empty] | 0.1352
26029000100 | [8 empty] | 0 | [21 empty] | 3
26049003300 | [30 empty] | 0.0021
26145000400 | [8 empty] | 0 | [21 empty] | 0.3207
26125123000 | [8 empty] | 0 | [21 empty] | 0.0152
26145012002 | [8 empty] | 0 | [21 empty] | 0.7714
26081003200 | [8 empty] | 0 | [21 empty] | 0.1286
26009960200 | [8 empty] | 0 | [6 empty] | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.5732
26023951400 | [8 empty] | 1
26119910300 | [8 empty] | 0
26111290900 | [8 empty] | 7 | [6 empty] | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.2701
26093713100 | [8 empty] | 0 | [21 empty] | 0.8235
26049013111 | [8 empty] | 0
26049003000 | [8 empty] | 0 | [6 empty] | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0012
26055551300 | [8 empty] | 0 | [21 empty] | 0.5373
26093713300 | [30 empty] | 0.5865
26037010702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 176 | 1 | 0.3784
26075006402 |  |  |  |  | 1 | 0.986 |  |  | 358 | [6 empty] | 71 | 2 | 0 | 0 | 0 | 0 | 23 | 0 | 1 | 44 | 1 | 3.64 | 0.02 | 169.85 | 0.9999 | 0.0838
26143970100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.03 | 0 | 65 | 1 | 0.0222
26081011701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.08 | 0 | 108.5 | 1 | 0.0004
26049002000 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | 0 | 891 | 1 | 0.043
26149041200 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.55 | 0 | 185 | 1 | 0.6662
26015011300 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 230.61 | 1 | 0.0042
26155031500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 210 | 192 | 0 | 0 | 0 | 0 | 16 | 2 | 0 | 0 | 0 | 11.93 | 0.07 | 174.81 | 0.9997 | 0.0666
26123970700 |  |  |  |  | 1 | 1 |  |  | 10 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2.52 | 0.02 | 168.05 | 0.9999 | 0.043
26005030702 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 33 | 2 | 1 | 0 | 0 | 0 | 24 | 5 | 0 | 1 | 0 | 2.62 | 0.01 | 179.34 | 0.9999 | 0.0632
26145001400 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 134.24 | 0.95 | 142 | 0.9969 | 0.0218
26031960100 |  |  |  |  | 1 | 0.97 |  |  | 0 | [6 empty] | 366 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 82.66 | 0.41 | 202.12 | 0.9981 | 0.0101
26081001200 |  |  |  |  | 1 | 0.694 | 1 |  | 0 | [6 empty] | 251 | 139 | 0 | 0 | 0 | 0 | 6 | 0 | 42 | 64 | 0 | 42.12 | 0.15 | 288.27 | 0.999 | 0.0186
26145010401 |  |  |  |  | 1 | 0.47 |  |  | 0 | [6 empty] | 1122 | 1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0.8 | 467.67 | 0.9913 | 0.995
26065005501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 371 | 1 | 0 | 366 | 0 | 0 | 3 | 0 | 1 | 0 | 0 | 0.29 | 0 | 130.3 | 1 | 0.1077
26139023200 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 315 | 0 | 243 | 0 | 0 | 69 | 0 | 2 | 1 | 0 | 0 | 56.82 | 0.34 | 164.88 | 0.9987 | 0.0558
26049010604 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 100 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 5.13 | 0.08 | 63.8 | 0.9999 | 0.1439
26005032401 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 113 | 1 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.95 | 1.12 | 103.64 | 0.9973 | 0.0099
26105950600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 135 | 3 | 0 | 86 | 0 | 0 | 7 | 8 | 0 | 31 | 0 | 1.21 | 0.02 | 50.74 | 1 | 0.018
26049002700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 137 | 4.84 | 0.09 | 55.61 | 0.9999 | 0.0592
26135970201 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 4.41 | 0.01 | 419.38 | 0.9999 | 0.0105
26049011712 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.39 | 0 | 330.67 | 1 | 0.0042
26165380200 |  |  |  |  | 1 | 1 |  |  | 398 | [6 empty] | 154 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 61 | 4.96 | 0.05 | 91.3 | 0.9999 | 0.1584
26127010300 |  |  |  |  | 1 | 0.667 |  |  | 1 | [6 empty] | 27 | 0 | 0 | 0 | 0 | 0 | 17 | 1 | 9 | 0 | 0 | 4.11 | 0.01 | 334.38 | 0.9999 | 0.0141
26049013001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 61 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 1 | 0 | 41 | 7.36 | 0.05 | 143.95 | 0.9998 | 0.0905
26139020400 |  |  |  |  | 1 | 1 | 1 |  | 18 | [6 empty] | 19 | 1 | 1 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 2.09 | 0.01 | 239.35 | 1 | 0.0488
26111291300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 27 | 12 | 1 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 2.93 | 0.01 | 213.29 | 0.9999 | 0.1808
26049010813 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 1.16 | 0.01 | 219.79 | 1 | 0.0317
26019000100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1.65 | 0.01 | 132.1 | 1 | 0.0125
26081013400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1406 | 47 | 0 | 0 | 0 | 1359 | 0 | 0 | 0 | 0 | 0 | 64.37 | 0.57 | 113.32 | 0.9985 | 0.0392
26077002905 |  |  |  |  | 1 |  | 1 |  | 753 | [6 empty] | 138 | 0 | 0 | 66 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 1.12 | 0.02 | 71 | 1 | 0.134
26015011400 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 67 | 59 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 5 | 2.21 | 0.02 | 90.24 | 0.9999 | 0.0095
26005031800 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 313 | 2 | 0 | 0 | 0 | 0 | 248 | 17 | 0 | 46 | 0 | 21.27 | 0.15 | 146.63 | 0.9995 | 0.2234
26049012006 |  |  |  |  | 1 | 0.929 |  |  | 0 | [6 empty] | 22 | 12 | 0 | 8 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 4.8 | 0.01 | 437.29 | 0.9999 | 0.0588
26049012202 |  |  |  |  | 1 | 0.833 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 1 | 3.93 | 0.01 | 456.07 | 0.9999 | 0.0503
26009960400 |  |  |  |  | 1 | 0.739 |  |  | 0 | [6 empty] | 299 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.02 | 0.13 | 452.84 | 0.9986 | 0.0239
26077000500 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5.02 | 0.01 | 677.74 | 0.9999 | 0.0019
26045021402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 2 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.29 | 0 | 104.07 | 1 | 0.0042
26107960200 |  |  |  |  | 1 | 1 | 1 |  | 44 | [6 empty] | 114 | 0 | 2 | 0 | 0 | 0 | 110 | 0 | 2 | 0 | 0 | 4.64 | 0.08 | 56.29 | 0.9999 | 0.5
26077001100 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 217 | 0 | 32 | 1 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 33.4 | 0.21 | 158.19 | 0.9992 | 0.1075
26057000500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0.17 | 0 | 69.76 | 1 | 0.004
26057000300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 0 | 308.15 | 1 | 0.0251
26091060600 |  |  |  |  | 1 | 0.442 |  |  | 4 | [6 empty] | 86 | 1 | 0 | 0 | 0 | 0 | 0 | 82 | 3 | 0 | 0 | 23.96 | 0.03 | 705.48 | 0.9994 | 0.8314
26073940200 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 41 | 8 | 1 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 1.82 | 0.02 | 114.53 | 1 | 0.0574
26081010904 |  |  |  |  | 1 | 0.992 |  |  | 1 | [6 empty] | 124 | 3 | 0 | 0 | 0 | 0 | 118 | 0 | 1 | 1 | 1 | 7.3 | 0.04 | 171.19 | 0.9998 | 0.0533
26091062400 |  |  |  |  | 1 | 0.449 | 1 |  | 60 | [6 empty] | 151 | 14 | 0 | 0 | 0 | 0 | 123 | 1 | 0 | 13 | 0 | 160.93 | 0.46 | 349.57 | 0.9963 | 1.4604
26133970300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 29 | 1 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 14.87 | 0.1 | 153.33 | 0.9997 | 0.0769
26031960700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 321 | 0 | 0 | 41 | 0 | 1 | 194 | 2 | 0 | 83 | 0 | 55.65 | 0.3 | 187.81 | 0.9987 | 0.2413
26081011804 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0.3 | 0 | 89.02 | 1
26139024400 |  |  |  |  | 1 | 0.988 |  |  | 0 | [6 empty] | 80 | 2 | 0 | 0 | 0 | 16 | 0 | 0 | 1 | 0 | 61 | 1.96 | 0.02 | 102.89 | 1 | 0.0238
26091061700 |  |  |  |  | 1 | 0.182 |  |  | 48 | [6 empty] | 11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1.48 | 0 | 456.83 | 1 | 0.0655
26117970500 |  |  |  |  | 1 | 1 |  |  | 26 | [6 empty] | 8 | 4 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0.75 | 0 | 271.54 | 1 | 0.9163
26085961200 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1.25 | 0 | 892 | 1
26029000300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.72 | 0 | 316.51 | 1 | 0.1162
26139024600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 120 | 0 | 6.96 | 0.05 | 142.39 | 0.9998 | 0.0019
26093721100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0 | 347 | 1 | 0.0035
26145001200 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 694 | 1 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 662 | 0 | 79.36 | 0.53 | 149.91 | 0.9982 | 0.032
26065006001 |  |  |  |  | 1 | 1 | 1 |  | 3 | [6 empty] | 127 | 112 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 0 | 35.61 | 0.11 | 314.28 | 0.9992 | 0.1276
26065005700 |  |  |  |  | 1 | 1 | 1 |  | 4 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.75 | 0.02 | 362.16 | 0.9999 | 0.0635
26115833800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 91 | 1 | 0.0144
26081012004 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0.74 | 0.04 | 17.72 | 1 | 0.0484
26121003500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 116 | 93 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 1 | 6.03 | 0.06 | 97.65 | 0.9999 | 0.0953
26081002300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 1.69 | 0.01 | 333.8 | 1 | 0.212
26051000100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2116 | 30 | 102 | 0 | 0 | 0 | 1982 | 0 | 0 | 2 | 0 | 129.97 | 0.59 | 220.63 | 0.997 | 1.669
26145010100 |  |  |  |  | 1 | 0.993 | 1 |  | 0 | [6 empty] | 715 | 600 | 0 | 0 | 0 | 84 | 27 | 2 | 0 | 1 | 1 | 32.21 | 0.17 | 193.37 | 0.9993 | 0.7025
26059051000 |  |  |  |  | 1 | 0.989 |  |  | 915 | [6 empty] | 88 | 14 | 1 | 0 | 0 | 0 | 65 | 0 | 0 | 8 | 0 | 7.66 | 0.05 | 165.59 | 0.9998 | 0.3043
26069000200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 81 | 2 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0.63 | 0.01 | 77.85 | 1 | 0.0863
26077000201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 31.58 | 0.18 | 172.63 | 0.9993 | 0.0062
26073000900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 156 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 95 | 48 | 7.22 | 0.08 | 87.94 | 0.9998 | 0.0316
26005032600 |  |  |  |  | 1 | 0 |  |  | 3 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.84 | 0.02 | 1050.68 | 0.9995
26051000500 |  |  |  |  | 1 | 1 | 1 |  | 66 | [6 empty] | 67 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 3.07 | 0.03 | 108.42 | 0.9999 | 0.1938
26081000700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 478 | 44 | 482 | 0 | 56.61 | 0.73 | 77.13 | 0.9987 | 0.0037
26049012009 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.22 | 0 | 459.64 | 0.9999
26101000700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 17 | 3 | 0 | 0 | 0 | 0 | 1 | 11 | 2 | 0 | 0 | 0.65 | 0.01 | 93.25 | 1 | 0.0107
26065006200 |  |  |  |  | 1 | 1 |  |  | 584 | [6 empty] | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0.65 | 0.01 | 101.67 | 1 | 0.3286
26037010701 |  |  |  |  | 1 | 1 | 1 |  | 12 | [6 empty] | 49 | 11 | 26 | 0 | 0 | 0 | 0 | 1 | 0 | 11 | 0 | 7.75 | 0.07 | 113.44 | 0.9998 | 0.0181
26139022001 |  |  |  |  | 1 | 0.8 | 1 |  | 0 | [6 empty] | 203 | 0 | 0 | 182 | 0 | 0 | 19 | 1 | 1 | 0 | 0 | 1.75 | 0.01 | 172.42 | 1 | 0.2651
26059050600 |  |  |  |  | 1 | 0.996 |  |  | 568 | [6 empty] | 277 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 168 | 38 | 69 | 28.76 | 0.18 | 159.8 | 0.9993 | 0.2339
26117970800 |  |  |  |  | 1 | 0.667 | 1 |  | 10 | [6 empty] | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 1 | 1 | 1.79 | 0.01 | 157.45 | 1 | 0.2485
26077001200 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 25 | 1 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3.19 | 0.02 | 181.4 | 0.9999 | 0.0162
26091060301 |  |  |  |  | 1 | 0.491 |  |  | 153 | [6 empty] | 350 | 29 | 1 | 0 | 0 | 0 | 316 | 4 | 0 | 0 | 0 | 75.16 | 0.17 | 447.97 | 0.9983 | 0.558
26073000500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 31 | 18 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.19 | 0.03 | 137.22 | 0.9999 | 0.0168
26081010903 |  |  |  |  | 1 | 1 | 1 |  | 4 | [6 empty] | 627 | 0 | 0 | 0 | 0 | 0 | 249 | 375 | 1 | 0 | 2 | 33.34 | 0.2 | 170.46 | 0.9992 | 0.0119
26077002901 |  |  |  |  | 1 | 1 | 1 |  | 210 | [6 empty] | 98 | 5 | 2 | 0 | 0 | 0 | 90 | 0 | 1 | 0 | 0 | 7.29 | 0.05 | 137.51 | 0.9998 | 0.0303
26111291101 |  |  |  |  | 1 | 0.014 |  |  | 540 | [6 empty] | 614 | 2 | 0 | 541 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 28.13 | 0.04 | 705.89 | 0.9993 | 0.3996
26145010600 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1122 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 1099 | 0 | 144.3 | 1.01 | 142.25 | 0.9967 | 0.0533
26049012401 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1.81 | 0.01 | 267.12 | 1 | 0.0023
26111291000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 113 | 1 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 95 | 0 | 4.88 | 0.04 | 131.02 | 0.9999 | 0.0016
26049011210 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 416 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 35.8 | 0.35 | 101.81 | 0.9992 | 0.1589
26035000800 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0.96 | 0.01 | 77.19 | 1 | 0.111
26049011502 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 78 | 25 | 46 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 4.77 | 0.05 | 99.79 | 0.9999 | 0.4703
26117970300 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 65 | 3 | 0 | 0 | 0 | 0 | 55 | 5 | 0 | 2 | 0 | 18.43 | 0.05 | 388.08 | 0.9996 | 0.263
26123970100 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 374 | 144 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 40.24 | 1.12 | 35.83 | 0.9991 | 0.5886
26115833900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 0.34 | 0 | 146.47 | 1 | 0.0066
26025001500 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0.01 | 150.5 | 1 | 0.0016
26101000400 |  |  |  |  | 1 | 1 |  |  | 56 | [6 empty] | 74 | 1 | 0 | 0 | 0 | 0 | 72 | 0 | 1 | 0 | 0 | 3.89 | 0.05 | 85.9 | 0.9999 | 0.0513
26059050300 |  |  |  |  | 1 | 1 | 1 |  | 266 | [6 empty] | 474 | 0 | 0 | 0 | 0 | 15 | 323 | 2 | 0 | 134 | 0 | 33.91 | 0.37 | 92.15 | 0.9992 | 0.045
26077000600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1276 | 0 | 0 | 0 | 0 | 0 | 0 | 1276 | 0 | 0 | 0 | 106.29 | 0.62 | 170.85 | 0.9975 | 0.2701
26121000900 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 0 | 577.18 | 1 | 0.0022
26115832700 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.06 | 0 | 74 | 1 | 0.0043
26093710100 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.55 | 0 | 545.15 | 1 | 0.002
26049002600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 19 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0.63 | 0.02 | 37.32 | 1 | 0.0284
26145011902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 122 | 79 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.57 | 0.07 | 224.51 | 0.9996 | 0.8534
26081011002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.23 | 0 | 284.04 | 1 | 0.0543
26115833200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 51 | 2 | 0 | 0 | 0 | 0 | 46 | 0 | 3 | 0 | 0 | 4.36 | 0.03 | 148.38 | 0.9999 | 0.0058
26081012201 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 395 | 10 | 0 | 0 | 0 | 0 | 377 | 1 | 6 | 1 | 0 | 9.56 | 0.12 | 78.02 | 0.9998 | 0.0447
26155030300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 109 | 2 | 1 | 3 | 0 | 0 | 71 | 27 | 1 | 4 | 0 | 4.06 | 0.04 | 99.48 | 0.9999 | 0.7891
26057000200 |  |  |  |  | 1 | 1 | 1 |  | 30 | [6 empty] | 132 | 94 | 2 | 0 | 0 | 0 | 0 | 23 | 13 | 0 | 0 | 7.13 | 0.05 | 132.87 | 0.9998 | 0.0988
26045021002 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 187 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 4.88 | 0.14 | 33.84 | 0.9999 | 0.0085
26081012608 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 569 | 1 | 0.0003
26139023001 |  |  |  |  | 1 | 0.964 | 1 |  | 0 | [6 empty] | 167 | 123 | 0 | 0 | 0 | 0 | 26 | 0 | 1 | 17 | 0 | 8.25 | 0.05 | 161.7 | 0.9998 | 0.059
26077002601 |  |  |  |  | 1 | 1 | 1 |  | 4 | [6 empty] | 40 | 1 | 0 | 24 | 0 | 0 | 7 | 0 | 8 | 0 | 0 | 0.83 | 0.01 | 148.67 | 1 | 0.1627
26081004500 |  |  |  |  | 1 | 0.929 |  |  | 0 | [6 empty] | 85 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 78 | 4.61 | 0.02 | 193.96 | 0.9999 | 0.0047
26011970400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 282 | 4 | 0 | 0 | 0 | 0 | 275 | 0 | 1 | 2 | 0 | 23.09 | 0.1 | 229.41 | 0.9995 | 0.3505
26081012701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 150 | 1 | 0.0018
26121002900 |  |  |  |  | 1 | 0.972 | 1 |  | 0 | [6 empty] | 189 | 3 | 1 | 0 | 0 | 0 | 161 | 0 | 1 | 23 | 0 | 13.04 | 0.08 | 162.29 | 0.9997 | 0.3418
26075006401 |  |  |  |  | 1 | 1 |  |  | 146 | [6 empty] | 51 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 7.79 | 0.03 | 232.89 | 0.9998 | 0.0262
26049010111 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.07 | 0.01 | 413.53 | 1
26159010100 |  |  |  |  | 1 | 0.993 | 1 |  | 246 | [6 empty] | 415 | 176 | 1 | 0 | 0 | 0 | 54 | 10 | 174 | 0 | 0 | 37.94 | 0.26 | 146.65 | 0.9991 | 0.0517
26049002300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 1.38 | 0.02 | 69.84 | 1 | 0.0084
26123970600 |  |  |  |  | 1 | 0.962 |  |  | 1 | [6 empty] | 26 | 8 | 1 | 0 | 0 | 0 | 14 | 0 | 2 | 1 | 0 | 1.78 | 0.02 | 110.32 | 1 | 0.1899
26049012501 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.59 | 0 | 530 | 1 | 0.0022
26125124000 |  |  |  |  | 1 | 1 |  |  | 32 | [6 empty] | 49 | 0 | 0 | 0 | 0 | 37 | 12 | 0 | 0 | 0 | 0 | 3.84 | 0.02 | 222.04 | 0.9999 | 0.053
26047970200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 2.25 | 0.01 | 191.53 | 0.9999 | 0.01
26005032100 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 202 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1 | 0 | 1 | 19.82 | 0.09 | 216.99 | 0.9995 | 0.1642
26017285100 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 32 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.36 | 0.02 | 69.9 | 1 | 0.0037
26025001000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 6 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0.5 | 0.01 | 83.31 | 1 | 0.8777
26089970100 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.42 | 0 | 390 | 1 | 0.0185
26045020404 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 85 | 24 | 0 | 37 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 1.43 | 0.02 | 65.88 | 1 | 0.0009
26049012601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1.41 | 0 | 451.03 | 1 | 0.0172
26123970800 |  |  |  |  | 1 | 1 | 1 |  | 531 | [6 empty] | 1065 | 1 | 0 | 0 | 0 | 0 | 1064 | 0 | 0 | 0 | 0 | 31.76 | 0.59 | 54.1 | 0.9993 | 0.4868
26143970600 |  |  |  |  | 1 | 0.61 | 1 |  | 0 | [6 empty] | 101 | 2 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 42 | 8.35 | 0.03 | 255.8 | 0.9998 | 0.0342
26115833700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0.22 | 0 | 108.99 | 1 | 0.0027
26145012700 |  |  |  |  | 1 | 0.933 |  |  | 0 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 1 | 0 | 1.02 | 0.01 | 165.57 | 1 | 0.9823
26031960800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 173 | 0 | 0 | 1 | 0 | 0 | 59 | 0 | 0 | 0 | 113 | 14.4 | 0.17 | 86.24 | 0.9997 | 0.1078
26121002601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.1 | 0 | 93.45 | 1 | 0.0021
26081012203 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 55 | 2 | 0 | 0 | 0 | 1 | 2 | 26 | 21 | 0 | 3 | 1.77 | 0.02 | 98.39 | 1 | 0.046
26077002801 |  |  |  |  | 1 | 1 | 1 |  | 83 | [6 empty] | 146 | 12 | 0 | 0 | 0 | 1 | 130 | 1 | 2 | 0 | 0 | 10.68 | 0.08 | 139.57 | 0.9998 | 0.2683
26081014803 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 127 | 2 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 35 | 0 | 13.2 | 0.08 | 156.92 | 0.9997 | 0.1013
26025000200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 143 | 1 | 0.0293
26081013900 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 281 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 255 | 0 | 10.66 | 0.1 | 112.13 | 0.9998 | 0.0041
26025003200 |  |  |  |  | 1 | 0.842 | 1 |  | 247 | [6 empty] | 345 | 25 | 0 | 1 | 0 | 0 | 286 | 33 | 0 | 0 | 0 | 83 | 0.3 | 279.63 | 0.9981 | 0.5306
26113960300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 509 | 1 | 237 | 0 | 0 | 0 | 34 | 0 | 0 | 10 | 227 | 29.19 | 0.2 | 149.2 | 0.9993 | 0.0634
26023951200 |  |  |  |  | 1 | 1 | 1 |  | 18 | [6 empty] | 29 | 1 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 1 | 13 | 1.09 | 0.01 | 78.88 | 1 | 0.0252
26075006500 |  |  |  |  | 1 | 0.027 | 1 |  | 80 | [6 empty] | 241 | 222 | 0 | 16 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 88.92 | 0.07 | 1196.63 | 0.9979 | 0.0472
26085961300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 51 | 1 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 7.49 | 0.06 | 122.05 | 0.9998 | 0.0638
26145001300 |  |  |  |  | 1 | 0.659 | 1 |  | 0 | [6 empty] | 261 | 3 | 0 | 0 | 0 | 0 | 109 | 23 | 0 | 126 | 0 | 62.61 | 0.23 | 266.74 | 0.9986 | 0.0063
26081012003 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 274 | 1 | 0 | 9 | 0 | 0 | 182 | 1 | 1 | 80 | 0 | 8.7 | 0.1 | 83.31 | 0.9998 | 0.9831
26065006401 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 159 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 156 | 0 | 0 | 9.65 | 0.09 | 103.13 | 0.9998 | 0.0059
26091060500 |  |  |  |  | 1 | 1 |  |  | 64 | [6 empty] | 78 | 10 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 2.47 | 0.07 | 37.47 | 0.9999 | 0.175
26081010301 |  |  |  |  | 1 | 0.991 | 1 |  | 180 | [6 empty] | 141 | 13 | 0 | 0 | 0 | 0 | 68 | 0 | 1 | 24 | 35 | 8.91 | 0.07 | 121.35 | 0.9998 | 0.0786
26037010500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 28 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 1.97 | 0.03 | 77.86 | 1 | 0.1056
26059050900 |  |  |  |  | 1 | 1 |  |  | 620 | [6 empty] | 29 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.72 | 0.02 | 176.23 | 0.9999 | 0.0342
26049010202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.54 | 0.01 | 279.39 | 0.9999 | 0.2107
26025003600 |  |  |  |  | 1 | 1 | 1 |  | 365 | [6 empty] | 391 | 0 | 0 | 0 | 0 | 0 | 17 | 374 | 0 | 0 | 0 | 37.54 | 0.3 | 124.54 | 0.9991 | 0.5906
26123970300 |  |  |  |  | 1 | 1 |  |  | 101 | [6 empty] | 1298 | 447 | 13 | 0 | 0 | 1 | 835 | 1 | 0 | 1 | 0 | 48.96 | 1 | 48.84 | 0.9989 | 0.7212
26049013401 |  |  |  |  | 1 | 0.8 |  |  | 0 | [6 empty] | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 205.45 | 1 | 0.0754
26017286100 |  |  |  |  | 1 | 0.4 |  |  | 72 | [6 empty] | 77 | 4 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.53 | 0 | 406.38 | 1 | 0.0122
26049011209 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 88 | 53 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 3.88 | 0.03 | 139.5 | 0.9999 | 0.0107
26049004000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 179 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5 | 0.12 | 98.93 | 0.9997 | 0.0104
26075005100 |  |  |  |  | 1 | 1 |  |  | 32 | [6 empty] | 31 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 0 | 15 | 0 | 0.85 | 0.01 | 110.64 | 1 | 0.0402
26081000900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.07 | 0 | 100.51 | 1 | 0.0576
26065004700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 145 | 0 | 0 | 1 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 10.15 | 0.08 | 121.62 | 0.9998 | 0.0151
26035000200 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 286 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 34.82 | 0.26 | 132.33 | 0.9992 | 0.4066
26121004200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 22 | 10 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 11 | 0 | 1.1 | 0.01 | 122.61 | 1 | 0.0106
26115833600 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.82 | 0 | 637.23 | 1 | 0.0174
26125124500 |  |  |  |  | 1 | 0.833 |  |  | 0 | [6 empty] | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 0.52 | 0 | 270.06 | 1 | 0.0022
26045020800 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 56 | 26 | 4 | 0 | 0 | 0 | 7 | 0 | 0 | 19 | 0 | 2.43 | 0.03 | 94.2 | 0.9999 | 0.0133
26067030100 |  |  |  |  | 1 | 1 | 1 |  | 104 | [6 empty] | 319 | 14 | 2 | 228 | 0 | 0 | 74 | 0 | 0 | 1 | 0 | 6.25 | 0.03 | 198.56 | 0.9999 | 0.1477
26049011101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 171 | 104 | 0 | 23 | 0 | 0 | 0 | 0 | 1 | 0 | 43 | 4.36 | 0.03 | 140.69 | 0.9999 | 0.0132
26165380100 |  |  |  |  | 1 | 1 |  |  | 60 | [6 empty] | 76 | 14 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 1 | 0 | 7.82 | 0.03 | 259.97 | 0.9998 | 0.093
26045020700 |  |  |  |  | 1 | 0.989 | 1 |  | 1 | [6 empty] | 103 | 43 | 3 | 0 | 0 | 47 | 0 | 9 | 0 | 0 | 1 | 11.67 | 0.06 | 179.57 | 0.9997 | 0.2391
26019000300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 0 | 251 | 1 | 0.0016
26077001803 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 52 | 0 | 44 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 3.4 | 0.05 | 73.89 | 0.9999 | 0.0044
26049013204 |  |  |  |  | 1 | 0.091 |  |  | 0 | [6 empty] | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 471.82 | 1 | 0.0046
26091061301 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 8 | 3.09 | 0.02 | 200.82 | 0.9999 | 0.0375
26067031400 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 97 | 0 | 40 | 0 | 0 | 0 | 56 | 0 | 1 | 0 | 0 | 51.25 | 0.36 | 142.11 | 0.9988 | 0.2825
26075000400 |  |  |  |  | 1 | 1 | 1 |  | 18 | [6 empty] | 70 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 55 | 2.36 | 0.04 | 55.81 | 0.9999 | 0.0048
26107960300 |  |  |  |  | 1 | 0.889 |  |  | 0 | [6 empty] | 10 | 1 | 0 | 1 | 0 | 0 | 6 | 0 | 2 | 0 | 0 | 1.73 | 0.01 | 268.05 | 1 | 0.1083
26133970200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 52 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 47 | 5.87 | 0.04 | 151.73 | 0.9999 | 0.0074
26143970700 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 241.31 | 1 | 0.0174
26077003003 |  |  |  |  | 1 | 1 |  |  | 741 | [6 empty] | 284 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 1 | 0 | 5.56 | 0.1 | 58.04 | 0.9999 | 0.0051
26155031402 |  |  |  |  | 1 | 0.765 | 1 |  | 0 | [6 empty] | 145 | 27 | 30 | 0 | 0 | 0 | 87 | 0 | 0 | 1 | 0 | 26.99 | 0.08 | 328.4 | 0.9994 | 0.119
26081012002 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 208 | 81 | 1 | 0 | 0 | 74 | 50 | 1 | 1 | 0 | 0 | 9.02 | 0.09 | 100.48 | 0.9998 | 0.0531
26081003600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 1.55 | 0.01 | 132.85 | 1 | 0.6543
26017285900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 502 | 366 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 1 | 97 | 11.98 | 0.2 | 60.93 | 0.9997 | 0.0133
26081014602 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 69 | 21 | 0 | 27 | 0 | 0 | 20 | 0 | 1 | 0 | 0 | 1.86 | 0.01 | 236.95 | 1 | 0.0676
26081003700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 20 | 1 | 0.9729
26057000600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 0.01 | 58.16 | 1
26091061400 |  |  |  |  | 1 | 1 |  |  | 22 | [6 empty] | 887 | 29 | 0 | 0 | 0 | 26 | 0 | 1 | 0 | 797 | 34 | 71.16 | 0.52 | 136.06 | 0.9984 | 0.1344
26123971200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 76 | 1 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 8.14 | 0.04 | 198.83 | 0.9998 | 0.0732
26091061900 |  |  |  |  | 1 | 1 | 1 |  | 204 | [6 empty] | 361 | 190 | 0 | 0 | 0 | 39 | 8 | 92 | 0 | 32 | 0 | 23.17 | 0.2 | 117.89 | 0.9995 | 0.0942
26081010302 |  |  |  |  | 1 | 1 | 1 |  | 26 | [6 empty] | 1490 | 386 | 9 | 0 | 0 | 0 | 101 | 0 | 2 | 37 | 955 | 46.71 | 0.67 | 69.25 | 0.9989 | 1.4156
26069000500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 92.76 | 1 | 0.1315
26081000600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 38 | 0 | 0 | 0 | 0 | 1 | 2 | 33 | 2 | 0 | 0 | 4.36 | 0.02 | 199.66 | 0.9999 | 0.0023
26145011901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 29 | 4 | 0 | 3.59 | 0.04 | 90.81 | 0.9999 | 0.9919
26145001500 |  |  |  |  | 1 | 0.418 |  |  | 0 | [6 empty] | 863 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250.1 | 0.54 | 461.07 | 0.9942 | 0.8737
26135970400 |  |  |  |  | 1 | 0.167 | 1 |  | 0 | [6 empty] | 241 | 0 | 1 | 0 | 0 | 0 | 239 | 0 | 0 | 1 | 0 | 76.99 | 0.15 | 530.65 | 0.9982 | 0.0006
26065006402 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 498 | 452 | 0 | 0 | 0 | 0 | 1 | 0 | 45 | 0 | 0 | 41.19 | 0.46 | 89.74 | 0.999 | 0.059
26015010600 |  |  |  |  | 1 | 1 | 1 |  | 447 | [6 empty] | 487 | 22 | 275 | 0 | 0 | 0 | 72 | 0 | 112 | 0 | 6 | 16.93 | 0.15 | 114.68 | 0.9996 | 0.4327
26005030200 |  |  |  |  | 1 | 0.981 |  |  | 33 | [6 empty] | 476 | 1 | 0 | 0 | 0 | 0 | 468 | 0 | 0 | 0 | 7 | 87.66 | 0.28 | 316.39 | 0.998 | 0.1653
26117970700 |  |  |  |  | 1 | 1 | 1 |  | 326 | [6 empty] | 297 | 42 | 191 | 0 | 0 | 0 | 20 | 4 | 0 | 34 | 6 | 14.51 | 0.12 | 123.62 | 0.9997 | 0.4067
26081001600 |  |  |  |  | 1 | 1 | 1 |  | 13 | [6 empty] | 2866 | 1 | 0 | 0 | 0 | 0 | 0 | 2132 | 0 | 733 | 0 | 93.15 | 1.08 | 86.1 | 0.9978 | 0.0038
26159012000 |  |  |  |  | 1 | 1 | 1 |  | 189 | [6 empty] | 151 | 0 | 80 | 0 | 0 | 0 | 68 | 1 | 0 | 2 | 0 | 25.86 | 0.17 | 155.13 | 0.9994 | 0.2494
26035000700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 95 | 1 | 1 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 5.24 | 0.03 | 149.84 | 0.9999 | 0.0998
26045021201 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 22 | 1 | 1 | 0 | 0 | 0 | 9 | 0 | 1 | 10 | 0 | 1.63 | 0.02 | 90.98 | 1
26049011212 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51 | 0.01 | 133.08 | 1 | 0.0021
26015010300 |  |  |  |  | 1 | 0.917 | 1 |  | 1 | [6 empty] | 17 | 1 | 3 | 0 | 0 | 1 | 2 | 0 | 2 | 6 | 2 | 0.87 | 0 | 192.53 | 1 | 0.4607
26049010304 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 0 | 248.78 | 1 | 0.0156
Census Tract Group 1 |  |  |  |  | 1 | 0.896 | 1 |  | 308 | [6 empty] | 1567 | 339 | 69 | 190 | 31 | 91 | 429 | 156 | 24 | 152 | 86 | 975.14 | 5.12 | 190.54 | 0.9774
26081012400 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 753 | 0 | 734 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 17 | 94.52 | 0.5 | 188.66 | 0.9978 | 0.2828
26081003300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 384 | 41 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.6 | 0.3 | 190.79 | 0.9987 | 0.3577
26121003800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 14 | 1 | 0 | 11 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.17 | 0 | 117.96 | 1 | 0.4937
26117971100 |  |  |  |  | 1 | 1 | 1 |  | 28 | [6 empty] | 312 | 187 | 1 | 14 | 0 | 0 | 16 | 0 | 1 | 93 | 0 | 28.22 | 0.12 | 230.29 | 0.9993 | 0.4778
26081014701 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 0 | 19.37 | 0.14 | 138.12 | 0.9996 | 0.5681
26145011701 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.79 | 0 | 638 | 1
26049000800 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 14.56 | 0.08 | 178.12 | 0.9997 | 0.0024
26065004802 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 695 | 0 | 0 | 0 | 0 | 0 | 695 | 0 | 0 | 0 | 0 | 62.73 | 0.47 | 134.31 | 0.9985 | 0.504
26075006803 |  |  |  |  | 1 | 1 | 1 |  | 818 | [6 empty] | 828 | 1 | 0 | 1 | 0 | 0 | 590 | 80 | 0 | 0 | 156 | 79.09 | 0.43 | 183.13 | 0.9982 | 0.8992
26133970600 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 399 | 0 | 0 | 1 | 0 | 0 | 0 | 215 | 0 | 183 | 0 | 36.81 | 0.22 | 167.14 | 0.9991 | 0.036
26049011711 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 96.93 | 0.06 | 1677.25 | 0.9978 | 0.0038
26005030901 |  |  |  |  | 1 | 1 |  |  | 3 | [6 empty] | 406 | 1 | 0 | 275 | 0 | 1 | 129 | 0 | 0 | 0 | 0 | 12.29 | 0.06 | 192.59 | 0.9997 | 0.6181
26039960500 |  |  |  |  | 1 | 0.988 | 1 |  | 0 | [6 empty] | 1087 | 3 | 1 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 840 | 49.37 | 0.72 | 68.17 | 0.9989 | 0.6982
26145010304 |  |  |  |  | 1 | 0.004 | 1 |  | 3 | [6 empty] | 1321 | 1312 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 1 | 197.29 | 0.38 | 515.09 | 0.9954 | 0.5344
26017286200 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 57 | 49 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.84 | 0.02 | 216.73 | 0.9999 | 0.018
26075006801 |  |  |  |  | 1 | 1 | 1 |  | 244 | [6 empty] | 66 | 26 | 0 | 0 | 0 | 0 | 0 | 12 | 2 | 26 | 0 | 3.39 | 0.04 | 88.21 | 0.9999 | 0.007
26081003500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 46 | 0 | 0 | 3 | 0 | 42 | 1 | 0 | 0 | 0 | 0 | 5.78 | 0.02 | 287.54 | 0.9999 | 0.1444
26155030200 |  |  |  |  | 1 | 0.667 | 1 |  | 0 | [6 empty] | 31 | 1 | 1 | 0 | 0 | 0 | 28 | 0 | 1 | 0 | 0 | 2.52 | 0.02 | 135.69 | 0.9999 | 0.6563
26081014704 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 604 | 0 | 0 | 0 | 0 | 0 | 0 | 575 | 29 | 0 | 0 | 70.15 | 0.52 | 134.62 | 0.9984 | 1.4702
26101000300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 110 | 0 | 52 | 0 | 0 | 0 | 13 | 1 | 1 | 0 | 43 | 7.97 | 0.06 | 136.4 | 0.9998 | 0.0484
26081013500 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1128 | 0 | 845 | 23 | 0 | 74 | 0 | 186 | 0 | 0 | 0 | 36.49 | 0.55 | 66.5 | 0.9992 | 0.0189
26057000700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 12 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 9 | 0 | 0 | 0.68 | 0.01 | 93.78 | 1 | 0.1081
26037010105 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 4.49 | 0.04 | 120.63 | 0.9999 | 1.0479
26049010114 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0.54 | 0.01 | 50.05 | 1 | 0.0425
26037010104 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.56 | 0 | 357.02 | 1 | 0.2482
26107960700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 93 | 5 | 0 | 0 | 0 | 0 | 86 | 1 | 0 | 1 | 0 | 2.54 | 0.04 | 70.8 | 0.9999 | 0.2371
26049003600 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 53 | 1 | 0 | 1 | 0 | 50 | 1 | 0 | 0 | 0 | 0 | 4.77 | 0.02 | 216.89 | 0.9999 | 0.9471
26161432000 |  |  |  |  | 1 | 1 | 1 |  | 59 | [6 empty] | 27 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 3.55 | 0.03 | 120.28 | 0.9999 | 0.6732
26081011301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 19 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 1.06 | 0.01 | 128.07 | 1 | 0.0004
26081002500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 528 | 0 | 0 | 0 | 0 | 0 | 528 | 0 | 0 | 0 | 0 | 21.13 | 0.19 | 108.75 | 0.9995 | 0.018
26049013301 |  |  |  |  | 1 | 0.833 | 1 |  | 12 | [6 empty] | 82 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0.02 | 179.55 | 0.9999 | 0.0208
26129950500 |  |  |  |  | 1 | 0.9 |  |  | 0 | [6 empty] | 20 | 3 | 0 | 0 | 0 | 0 | 4 | 0 | 1 | 12 | 0 | 1.1 | 0.01 | 161.08 | 1 | 0.0393
26115832800 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.21 | 0 | 140 | 1 | 0.0074
26077001801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 67 | 0 | 66 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4.31 | 0.04 | 98.42 | 0.9999 | 0.6033
26081014502 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 41 | 0 | 46 | 5.2 | 0.04 | 130.63 | 0.9999 | 0.0068
26067031200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 65 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 6.81 | 0.04 | 172.98 | 0.9998 | 0.0418
26139023100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.14 | 0 | 142.44 | 1
26081003400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 106 | 1 | 0.0238
26035000900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0.22 | 0 | 114.62 | 1 | 0.0039
26139021700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.08 | 0 | 146.7 | 1 | 0.0033
26047970500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 96 | 0 | 0 | 0 | 0 | 79 | 17 | 0 | 0 | 0 | 0 | 8.93 | 0.08 | 110.9 | 0.9998 | 0.0369
26101000500 |  |  |  |  | 1 | 1 |  |  | 40 | [6 empty] | 426 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 1 | 321 | 5 | 19.95 | 0.28 | 70.4 | 0.9995 | 0.5416
26111290300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 80 | 4 | 0 | 1 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 10.56 | 0.04 | 242.5 | 0.9998 | 0.5695
26081001900 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 131 | 5 | 0 | 0 | 0 | 0 | 0 | 125 | 1 | 0 | 0 | 4.37 | 0.04 | 98.72 | 0.9999 | 0.003
26073000100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 180 | 136 | 18 | 0 | 0 | 0 | 1 | 1 | 0 | 24 | 0 | 22.48 | 0.2 | 112.52 | 0.9995 | 0.0433
26049002400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 0 | 116 | 1 | 0.0173
26075001200 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 191 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 15.25 | 0.13 | 116.47 | 0.9996 | 0.092
26081014804 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.13 | 0 | 55.15 | 1 | 0.014
26029001100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.04 | 0 | 18.94 | 1 | 0.001
26081012901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 630 | 0 | 0 | 162 | 0 | 0 | 0 | 157 | 0 | 311 | 0 | 30.52 | 0.21 | 147.16 | 0.9993 | 0.0022
26091061302 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 43 | 27.36 | 0.21 | 133.38 | 0.9994 | 0.0125
26105950400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0.14 | 0 | 60.73 | 1 | 0.0012
26145013100 |  |  |  |  | 1 | 0.3 | 1 |  | 0 | [6 empty] | 14 | 9 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.55 | 0 | 348.43 | 1 | 0.0038
26117971200 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 97 | 5 | 32 | 0 | 0 | 0 | 0 | 2 | 0 | 35 | 23 | 5.63 | 0.03 | 161.92 | 0.9999 | 0.0915
26081002700 |  |  |  |  | 1 | 0.833 |  |  | 0 | [6 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 0 | 0 | 0.73 | 0 | 217.47 | 1 | 0.0039
26049010912 |  |  |  |  | 1 | 0.978 | 1 |  | 0 | [6 empty] | 91 | 1 | 1 | 6 | 0 | 0 | 0 | 39 | 0 | 0 | 44 | 1.83 | 0.04 | 47.39 | 1 | 0.0331
26145010501 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1184 | 0 | 0 | 17 | 0 | 0 | 1 | 0 | 0 | 1166 | 0 | 142.48 | 1 | 142.6 | 0.9967 | 0.0214
26067031600 |  |  |  |  | 1 | 1 | 1 |  | 6 | [6 empty] | 234 | 0 | 127 | 63 | 0 | 0 | 23 | 14 | 0 | 7 | 0 | 7.53 | 0.07 | 107.44 | 0.9998 | 0.423
26133970500 |  |  |  |  | 1 | 0.955 |  |  | 36 | [6 empty] | 44 | 31 | 0 | 0 | 0 | 0 | 5 | 0 | 3 | 4 | 1 | 3.68 | 0.03 | 137.11 | 0.9999 | 0.0506
26145002000 |  |  |  |  | 1 | 0 | 1 |  | 0 | [6 empty] | 1401 | 1391 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 451.33 | 0.88 | 512.54 | 0.9896 | 1.4004
26075006600 |  |  |  |  | 1 | 0.112 | 1 |  | 87 | [6 empty] | 1162 | 912 | 1 | 0 | 0 | 0 | 161 | 0 | 0 | 9 | 79 | 554.16 | 0.55 | 1006.26 | 0.9872 | 0.0445
26025001300 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 11 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1.23 | 0 | 248.71 | 1 | 0.0673
26035001000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 80 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 1 | 3.55 | 0.04 | 95.07 | 0.9999 | 0.0215
26117970900 |  |  |  |  | 1 | 1 |  |  | 10 | [6 empty] | 23 | 6 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 6 | 1.21 | 0.01 | 109.34 | 1 | 0.1637
26081004000 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 68 | 0 | 67 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.39 | 0.06 | 56.48 | 0.9999 | 0.1354
26115832400 |  |  |  |  | 1 | 1 |  |  | 10 | [6 empty] | 717 | 708 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8 | 21.38 | 0.42 | 51.05 | 0.9995 | 0.0158
26121001800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.03 | 0 | 63.63 | 1 | 0.0014
26077003500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.08 | 0 | 95 | 1 | 0.0095
26037010901 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 23 | 16 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.59 | 0.02 | 144.91 | 0.9999 | 0.4029
26143971000 |  |  |  |  | 1 | 0.984 |  |  | 0 | [6 empty] | 63 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 5 | 1 | 3.17 | 0.02 | 161.56 | 0.9999 | 0.5418
26101000100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 32 | 1 | 2.74 | 0.04 | 66.02 | 0.9999 | 1.1694
26081011101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 163 | 1 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 1 | 0 | 9.66 | 0.07 | 129.62 | 0.9998 | 0.0032
26085960100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 76 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 33.41 | 0.32 | 103.76 | 0.9992 | 0.8305
26091062200 |  |  |  |  | 1 | 0.999 |  |  | 1 | [6 empty] | 1249 | 1236 | 0 | 0 | 0 | 0 | 0 | 11 | 1 | 1 | 0 | 150.92 | 1 | 151.16 | 0.9965 | 0.1351
26025000500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 49 | 21 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 5.58 | 0.04 | 159.09 | 0.9999 | 0.0107
26005031300 |  |  |  |  | 1 | 0.969 | 1 |  | 18 | [6 empty] | 175 | 0 | 1 | 0 | 0 | 0 | 102 | 37 | 0 | 0 | 35 | 17.68 | 0.09 | 188.98 | 0.9996 | 0.202
26091062000 |  |  |  |  | 1 | 1 | 1 |  | 13 | [6 empty] | 135 | 69 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 0 | 17.59 | 0.13 | 139.06 | 0.9996 | 1.3899
26121003300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 43 | 5 | 0 | 0 | 0 | 0 | 37 | 1 | 0 | 0 | 0 | 2.57 | 0.02 | 147.02 | 0.9999 | 0.0219
26077005502 |  |  |  |  | 1 | 0.286 |  |  | 0 | [6 empty] | 21 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10.71 | 0.01 | 1424.12 | 0.9998 | 0.0154
26143970200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.19 | 0 | 166.94 | 1 | 0.1542
26091060402 |  |  |  |  | 1 | 0.891 |  |  | 338 | [6 empty] | 733 | 82 | 0 | 0 | 0 | 0 | 325 | 1 | 318 | 4 | 3 | 45.56 | 0.31 | 148.79 | 0.9989 | 0.6437
26031960200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 274 | 1 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.13 | 0.17 | 164.47 | 0.9993 | 0.0025
26121002300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 290 | 2 | 0 | 277 | 0 | 0 | 2 | 0 | 7 | 1 | 1 | 0.46 | 0.01 | 89.74 | 1
26049001000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 222 | 0 | 0 | 14 | 0 | 207 | 1 | 0 | 0 | 0 | 0 | 56.03 | 0.26 | 215.24 | 0.9987 | 0.0576
26165380500 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 30 | 0 | 2 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 0 | 0.8 | 0.01 | 100.37 | 1 | 0.0051
26019000500 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 321 | 191 | 0 | 0 | 0 | 0 | 58 | 72 | 0 | 0 | 0 | 13.11 | 0.15 | 88.04 | 0.9997 | 0.2729
26049011902 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.08 | 0 | 113.52 | 1 | 0.0035
26081000500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.02 | 0 | 36.98 | 1 | 0.0098
26057001000 |  |  |  |  | 1 | 1 | 1 |  | 118 | [6 empty] | 76 | 3 | 0 | 0 | 0 | 13 | 0 | 21 | 39 | 0 | 0 | 4.6 | 0.04 | 123.91 | 0.9999 | 0.0044
26115833300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.85 | 0 | 263.03 | 1 | 0.0023
26025001700 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0.01 | 26.63 | 1 | 0.0062
26115832300 |  |  |  |  | 1 | 1 |  |  | 4 | [6 empty] | 275 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9 | 1 | 63.13 | 0.9985 | 0.029
26049010504 |  |  |  |  | 1 | 1 | 1 |  | 40 | [6 empty] | 47 | 27 | 0 | 0 | 0 | 2 | 0 | 18 | 0 | 0 | 0 | 5.46 | 0.02 | 219.13 | 0.9999 | 0.0042
26081010102 |  |  |  |  | 1 | 0.998 | 1 |  | 29 | [6 empty] | 627 | 1 | 29 | 0 | 0 | 0 | 595 | 1 | 0 | 1 | 0 | 114.86 | 0.46 | 249.7 | 0.9973 | 0.3412
26079950300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.12 | 0 | 87.61 | 1 | 0.002
26049000100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 1 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0 | 411.3 | 1 | 0.0123
26139022107 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 237 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 0 | 0 | 0 | 131.67 | 0.3 | 437.22 | 0.997 | 0.2224
26139021604 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 1 | 0 | 0 | 9.61 | 0.07 | 147.16 | 0.9998 | 0.0021
26025003500 |  |  |  |  | 1 | 1 | 1 |  | 39 | [6 empty] | 68 | 0 | 26 | 0 | 0 | 1 | 0 | 40 | 0 | 0 | 1 | 8.25 | 0.07 | 125.25 | 0.9998 | 0.4008
26049001600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 18 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.01 | 18.6 | 1 | 0.2714
26107960500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 42 | 4 | 0 | 0 | 0 | 0 | 36 | 0 | 2 | 0 | 0 | 2.29 | 0.02 | 108.28 | 0.9999 | 0.0721
26011970100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 160.03 | 1 | 0.1028
26077006702 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 40 | 2 | 0 | 0 | 0 | 30 | 6 | 0 | 0 | 2 | 0 | 2.39 | 0.01 | 181.3 | 0.9999 | 0.0485
26089970500 |  |  |  |  | 1 | 0.999 | 1 |  | 0 | [6 empty] | 1158 | 185 | 0 | 279 | 0 | 0 | 678 | 16 | 0 | 0 | 0 | 59.99 | 0.35 | 169.4 | 0.9986 | 0.498
26111290600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 25 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.53 | 0.02 | 154.99 | 0.9999 | 0.2356
26075000900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 0.02 | 69.89 | 1 | 0.0421
26049010811 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.65 | 0.01 | 229.1 | 1 | 0.0045
26049012703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 58 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 2.57 | 0.04 | 67.27 | 0.9999 | 0.0256
26123971000 |  |  |  |  | 1 | 1 |  |  | 134 | [6 empty] | 30 | 1 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 1.3 | 0.01 | 97.93 | 1 | 0.067
26077001906 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 13 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.47 | 0 | 99.82 | 1 | 0.004
26091061500 |  |  |  |  | 1 | 1 |  |  | 212 | [6 empty] | 733 | 44 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 632 | 0 | 40.82 | 0.32 | 126.65 | 0.9991 | 0.0211
26145011800 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 7 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 2.6 | 0.01 | 372.73 | 0.9999 | 0.1871
26081000800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 42 | 1 | 0 | 26 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0.88 | 0.01 | 85.48 | 1 | 0.1096
26115832900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0.29 | 240 | 0.9984 | 0.1944
26127011000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 19 | 1 | 0.0045
26029001000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.15 | 0.01 | 18.94 | 1 | 0.0032
26049010610 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 191 | 166 | 0 | 0 | 0 | 0 | 12 | 0 | 13 | 0 | 0 | 21.49 | 0.08 | 258.84 | 0.9995 | 0.0048
26037010902 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 40 | 1 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3.23 | 0.02 | 147.3 | 0.9999 | 0.8661
26117970400 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0.01 | 201.9 | 1 | 0.6437
26081010200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 88 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 64 | 1.89 | 0.04 | 42.19 | 1 | 0.086
26029000200 |  |  |  |  | 1 | 0.881 |  |  | 0 | [6 empty] | 413 | 1 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 146.79 | 0.67 | 217.51 | 0.9966 | 0.6078
26065005401 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 117 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.09 | 0.07 | 99.79 | 0.9998 | 0.1659
26005030703 |  |  |  |  | 1 | 0.999 | 1 |  | 1 | [6 empty] | 1011 | 0 | 0 | 0 | 0 | 18 | 986 | 0 | 1 | 0 | 6 | 140.48 | 0.78 | 180.5 | 0.9967 | 0.3041
26121000800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.06 | 0 | 94.05 | 1 | 0.0012
26025001800 |  |  |  |  | 1 | 1 |  |  | 3 | [6 empty] | 13 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 11 | 0 | 1 | 0.54 | 0 | 144.49 | 1 | 0.0038
26081014807 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 132 | 3 | 0 | 1 | 0 | 0 | 58 | 66 | 2 | 1 | 1 | 10.13 | 0.03 | 326.86 | 0.9998 | 0.0289
26139021901 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 338 | 0 | 2 | 290 | 0 | 1 | 42 | 0 | 0 | 3 | 0 | 2.84 | 0.03 | 96.13 | 0.9999 | 0.0431
26069000600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0 | 474 | 1 | 0.1438
26155030100 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 27 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 1 | 1.25 | 0.01 | 127.1 | 1 | 0.3404
26049010603 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 94 | 8 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 68 | 5.55 | 0.03 | 169.67 | 0.9999 | 0.0073
26069000900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 398 | 0 | 0 | 16 | 0 | 0 | 36 | 0 | 0 | 0 | 346 | 45.92 | 0.16 | 284.18 | 0.9989 | 0.0385
26081011102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 45 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 1.8 | 0.02 | 91.5 | 1 | 0.007
26133970400 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 50 | 3 | 1 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 6.9 | 0.04 | 171.56 | 0.9998 | 0.328
26091060800 |  |  |  |  | 1 | 0.371 |  |  | 2 | [6 empty] | 62 | 11 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 18 | 0 | 17.86 | 0.03 | 523.99 | 0.9996 | 0.2578
26091061200 |  |  |  |  | 1 | 1 |  |  | 110 | [6 empty] | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.62 | 0.06 | 145.24 | 0.9998 | 0.997
26111290400 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 108 | 1 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 5 | 0 | 15.86 | 0.12 | 132.6 | 0.9996 | 0.6977
26115833100 |  |  |  |  | 1 | 0.85 |  |  | 7 | [6 empty] | 21 | 1 | 0 | 1 | 0 | 3 | 15 | 0 | 1 | 0 | 0 | 2.46 | 0.01 | 278.37 | 0.9999 | 0.0066
26073000600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 42 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.74 | 0.02 | 96.19 | 1 | 0.1488
26065003801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.69 | 0 | 364 | 1
26005032402 |  |  |  |  | 1 | 1 | 1 |  | 22 | [6 empty] | 124 | 0 | 83 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 8.68 | 0.07 | 127.52 | 0.9998 | 0.0456
26025003100 |  |  |  |  | 1 | 1 |  |  | 227 | [6 empty] | 87 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 1 | 0 | 0 | 4.63 | 0.07 | 70.65 | 0.9999 | 0.0444
26081010902 |  |  |  |  | 1 | 1 | 1 |  | 34 | [6 empty] | 926 | 336 | 27 | 0 | 0 | 0 | 1 | 84 | 0 | 476 | 2 | 72.45 | 0.46 | 158.51 | 0.9983 | 0.3342
26077003400 |  |  |  |  | 1 | 1 | 1 |  | 25 | [6 empty] | 15 | 7 | 1 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0.68 | 0.01 | 76.88 | 1 | 0.0012
26145001800 |  |  |  |  | 1 | 0.005 |  |  | 0 | [6 empty] | 203 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.29 | 0.24 | 515.37 | 0.9971 | 1.8635
26077001503 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.01 | 54.54 | 1 | 0.1992
26121001500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.16 | 0 | 312.11 | 1 | 0.001
26081014601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 351 | 0 | 0 | 1 | 0 | 0 | 69 | 278 | 0 | 1 | 2 | 16.41 | 0.08 | 211.92 | 0.9996 | 0.0387
26139021304 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 5.13 | 0.01 | 577.13 | 0.9999 | 0.0032
26111291400 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 288 | 42 | 0 | 1 | 0 | 0 | 28 | 0 | 0 | 9 | 208 | 12.13 | 0.14 | 85.14 | 0.9997 | 0.069
26145013000 |  |  |  |  | 1 | 0.857 | 1 |  | 0 | [6 empty] | 8 | 7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.62 | 0 | 385.57 | 1 | 0.706
26159011300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 187 | 0 | 0 | 0 | 0 | 0 | 186 | 1 | 0 | 0 | 0 | 31.13 | 0.14 | 227.05 | 0.9993 | 0.0374
26055550200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 187 | 36 | 0 | 150 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 16.77 | 0.09 | 190.77 | 0.9996
26081001400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 49 | 34 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 3.33 | 0.02 | 142.71 | 0.9999 | 0.0048
26065005502 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 42 | 1 | 39 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2.73 | 0.01 | 202.5 | 0.9999 | 0.1653
26023950100 |  |  |  |  | 1 | 1 | 1 |  | 243 | [6 empty] | 224 | 1 | 0 | 0 | 0 | 1 | 187 | 35 | 0 | 0 | 0 | 10.73 | 0.12 | 91.07 | 0.9998 | 0.2267
26105950500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 51 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0.13 | 0.01 | 9.93 | 1 | 0.0028
26093710300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 30 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1 | 0 | 1.57 | 0.01 | 121.46 | 1 | 0.2336
26155031301 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 43 | 0 | 10 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 1 | 4.58 | 0.02 | 198.46 | 0.9999 | 0.0285
26081010401 |  |  |  |  | 1 | 1 | 1 |  | 56 | [6 empty] | 167 | 0 | 1 | 0 | 0 | 0 | 62 | 104 | 0 | 0 | 0 | 8.74 | 0.07 | 119.35 | 0.9998 | 0.1105
26051000700 |  |  |  |  | 1 | 1 | 1 |  | 5 | [6 empty] | 41 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 1.12 | 0.02 | 70.45 | 1 | 0.0982
26001970600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 151 | 0 | 0 | 0 | 0 | 91 | 60 | 0 | 0 | 0 | 0 | 12.59 | 0.09 | 143.21 | 0.9997 | 0.4721
26113960100 |  |  |  |  | 1 | 0.999 | 1 |  | 0 | [6 empty] | 1128 | 1 | 0 | 114 | 0 | 0 | 1001 | 3 | 0 | 0 | 9 | 25.2 | 0.37 | 68.11 | 0.9994 | 0.7234
26081014806 |  |  |  |  | 1 | 0.875 | 1 |  | 0 | [6 empty] | 9 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.57 | 0 | 154.24 | 1 | 0.3129
26037010600 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1.28 | 0 | 399.5 | 1 | 0.0385
26091060401 |  |  |  |  | 1 | 1 |  |  | 88 | [6 empty] | 246 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 243 | 1 | 1 | 12.68 | 0.13 | 95.85 | 0.9997 | 0.1538
26101000200 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 107 | 0 | 49 | 0 | 0 | 0 | 1 | 2 | 1 | 45 | 9 | 7.07 | 0.06 | 124.16 | 0.9998 | 0.2831
26117970200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 39 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4.67 | 0.02 | 190.44 | 0.9999 | 0.0138
26081011600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 120 | 0 | 0 | 0 | 0 | 0 | 1 | 104 | 1 | 14 | 0 | 6.06 | 0.03 | 194.27 | 0.9999 | 0.0125
26121003000 |  |  |  |  | 1 | 0.958 | 1 |  | 100 | [6 empty] | 80 | 1 | 1 | 0 | 0 | 0 | 21 | 0 | 1 | 1 | 55 | 2.23 | 0.05 | 44.42 | 0.9999 | 0.0013
26115832500 |  |  |  |  | 1 | 0.984 |  |  | 10 | [6 empty] | 856 | 831 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 0 | 0 | 64.89 | 0.37 | 173.81 | 0.9985 | 0.0249
26123970500 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0.21 | 0 | 287.75 | 1 | 0.012
26165380300 |  |  |  |  | 1 | 1 | 1 |  | 38 | [6 empty] | 707 | 2 | 10 | 1 | 0 | 0 | 692 | 2 | 0 | 0 | 0 | 33.57 | 0.32 | 105.05 | 0.9992 | 1.1684
26139025500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1.03 | 0.01 | 145.04 | 1 | 0.0035
26015010100 |  |  |  |  | 1 | 0.993 | 1 |  | 9 | [6 empty] | 257 | 96 | 1 | 59 | 0 | 45 | 18 | 0 | 38 | 0 | 0 | 11.56 | 0.07 | 167.27 | 0.9997 | 0.1913
26081011200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 0.01 | 119.63 | 1 | 0.064
26077002904 |  |  |  |  | 1 | 1 |  |  | 413 | [6 empty] | 51 | 1 | 0 | 0 | 0 | 0 | 13 | 1 | 1 | 35 | 0 | 1.22 | 0.01 | 106.7 | 1 | 0.3612
26049011503 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 96 | 0 | 82 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.61 | 0.04 | 128.69 | 0.9999 | 0.2001
26049012904 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 395.02 | 1 | 0.0016
26025003000 |  |  |  |  | 1 | 1 | 1 |  | 106 | [6 empty] | 56 | 1 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 4.43 | 0.05 | 82.56 | 0.9999 | 0.0709
26139020504 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 21.45 | 0.07 | 301.29 | 0.9995 | 0.0032
26161447000 |  |  |  |  | 1 |  | 1 |  | 345 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.15 | 0 | 207.85 | 1 | 0.3543
26073940300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.04 | 0 | 125 | 1 | 0.0743
26073000700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 83 | 1 | 0.186
26121004300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.14 | 0 | 145.8 | 1 | 0.0039
26017286400 |  |  |  |  | 1 | 1 |  |  | 13 | [6 empty] | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.58 | 0.02 | 78.44 | 1 | 0.1206
26145010700 |  |  |  |  | 1 | 0.294 |  |  | 0 | [6 empty] | 34 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 5.19 | 0.01 | 432.31 | 0.9999 | 1.9527
26077001502 |  |  |  |  | 1 | 0.684 |  |  | 2 | [6 empty] | 311 | 310 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.46 | 0.12 | 313.9 | 0.9991 | 0.9388
26075006804 |  |  |  |  | 1 | 0.977 | 1 |  | 141 | [6 empty] | 107 | 13 | 0 | 0 | 0 | 0 | 71 | 0 | 2 | 21 | 0 | 7.94 | 0.04 | 221.41 | 0.9998 | 0.0473
26139021802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 18 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0.76 | 0.01 | 101.53 | 1 | 0.104
26049013110 |  |  |  |  | 1 | 0.6 |  |  | 0 | [6 empty] | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1.36 | 0 | 297.6 | 1
26075001000 | [8 empty] | 0 | [21 empty] | 0.0121
26125126400
26077002003 | [8 empty] | 1 | [21 empty] | 0.0008
26031960500 | [8 empty] | 0 | [6 empty] | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.293
26121001300 | [8 empty] | 0 | [21 empty] | 0.0011
26081000100 | [8 empty] | 0 | [21 empty] | 0.5995
26139021603 | [30 empty] | 0.0005
26075005000 | [8 empty] | 53 | [21 empty] | 0.0027
26055550102 | [8 empty] | 0 | [6 empty] | 1112 | 0 | 0 | 1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.6834
26089970200 | [8 empty] | 0 | [21 empty] | 0.1304
26145000600 | [8 empty] | 0 | [21 empty] | 0.1542
26081012604 | [8 empty] | 0 | [6 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.0017
26049012504 | [8 empty] | 0 | [21 empty] | 0.3068
26049003500 | [8 empty] | 0 | [21 empty] | 0.023
26165380600 | [8 empty] | 0
26139022103 | [8 empty] | 0 | [21 empty] | 0.0084
26049000400 | [8 empty] | 0 | [6 empty] | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.1905
26037010201 | [8 empty] | 0 | [21 empty] | 0.0375
26049013112 | [8 empty] | 0 | [21 empty] | 0.0034
26145010800 | [8 empty] | 0 | [21 empty] | 0.2354
26081013802 | [8 empty] | 0 | [21 empty] | 0.1086
26049013600 | [8 empty] | 0 | [21 empty] | 0.0013
26025004000 | [8 empty] | 50
26155031600 | [8 empty] | 0 | [6 empty] | 491 | 0 | 0 | 491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.565
26065005402 | [8 empty] | 0 | [21 empty] | 0.4183
26075001100 | [8 empty] | 1 | [21 empty] | 0.0033
26059050500 | [8 empty] | 48 | [21 empty] | 0.0486
26037010107 | [8 empty] | 0 | [21 empty] | 0.7502
26049000500 | [8 empty] | 0 | [21 empty] | 0.1364
26065004902 | [8 empty] | 0 | [21 empty] | 0.0085
26075005900 | [8 empty] | 0 | [21 empty] | 0.0013
26139020600
26139021202 | [8 empty] | 0
26055551100 | [8 empty] | 0 | [21 empty] | 0.4217
26049013402 | [8 empty] | 0 | [21 empty] | 0.3516
26081000300 | [8 empty] | 0 | [21 empty] | 0.0015
26025004100 | [8 empty] | 0 | [21 empty] | 0.0041
26037010801 | [8 empty] | 0 | [21 empty] | 0.0028
26077000100 | [8 empty] | 0 | [21 empty] | 0.0039
26073000200 | [8 empty] | 0
26065005001 | [8 empty] | 0 | [21 empty] | 0.003
26081011302 | [8 empty] | 0 | [21 empty] | 0.0006
26121003900 | [8 empty] | 0 | [21 empty] | 0.2691
26137950300 |  |  |  |  | 1 | 1 | 1 |  | 107 | [6 empty] | 2610 | 2609 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.97 | 0.68 | 223.76 | 0.9965 | 0.0814
26111291602 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 16 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 5 | 1 | 0.71 | 0.01 | 107.33 | 1 | 0.0046
26075006701 |  |  |  |  | 1 | 0.95 | 1 |  | 22 | [6 empty] | 163 | 107 | 0 | 0 | 0 | 0 | 31 | 24 | 1 | 0 | 0 | 20.25 | 0.07 | 293.12 | 0.9995 | 0.0958
26121002200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0.38 | 0 | 92.23 | 1 | 0.0005
26145012200 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 11 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.63 | 0.01 | 48.19 | 1 | 0.0012
26025002700 |  |  |  |  | 1 | 1 | 1 |  | 184 | [6 empty] | 372 | 62 | 0 | 0 | 0 | 0 | 260 | 49 | 1 | 0 | 0 | 15.47 | 0.12 | 129.23 | 0.9996 | 0.0302
26123970400 |  |  |  |  | 1 | 1 |  |  | 5 | [6 empty] | 56 | 14 | 0 | 8 | 0 | 0 | 30 | 0 | 4 | 0 | 0 | 0.86 | 0.02 | 43.83 | 1 | 0.122
26145010403 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 592 | 0 | 53 | 358 | 0 | 0 | 0 | 1 | 0 | 179 | 1 | 10.41 | 0.08 | 129.37 | 0.9998 | 0.6918
26035000400 |  |  |  |  | 1 | 0.996 |  |  | 129 | [6 empty] | 260 | 118 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 136 | 1 | 17.55 | 0.12 | 147.76 | 0.9996 | 0.3065
26015010500 |  |  |  |  | 1 | 1 | 1 |  | 5 | [6 empty] | 299 | 1 | 3 | 0 | 0 | 0 | 294 | 0 | 1 | 0 | 0 | 51.3 | 0.16 | 330.14 | 0.9988 | 0.3784
26081012702 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | 0 | 183.5 | 1 | 0.1309
26091060302 |  |  |  |  | 1 | 0.846 |  |  | 208 | [6 empty] | 39 | 2 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 5.74 | 0.01 | 430.24 | 0.9999 | 0.0154
26145010502 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1958 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 8 | 1602 | 1 | 78.12 | 0.59 | 132.71 | 0.9982 | 0.1461
26005030401 |  |  |  |  | 1 | 1 | 0.995 |  | 0 | [6 empty] | 1444 | 1361 | 0 | 0 | 0 | 0 | 43 | 4 | 0 | 36 | 0 | 126.58 | 0.53 | 238.7 | 0.9971 | 0.3768
26139021303 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 27 | 0 | 2 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 4.67 | 0.02 | 198.22 | 0.9999 | 0.0837
26089970300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 109 | 1 | 0 | 0 | 0 | 18 | 89 | 0 | 0 | 1 | 0 | 19.92 | 0.05 | 374.76 | 0.9995 | 0.02
26045020500 |  |  |  |  | 1 | 1 |  |  | 33 | [6 empty] | 145 | 8 | 0 | 129 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0.84 | 0.01 | 65.88 | 1 | 0.0287
26049000300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 39 | 0 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 14 | 1 | 6.47 | 0.03 | 244.02 | 0.9999 | 0.0039
26165380700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 7.8 | 0.1 | 76.77 | 0.9998 | 0.0239
26121002602 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 49 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 15 | 16 | 0 | 2.51 | 0.02 | 132.68 | 0.9999 | 0.0081
26001970400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1034 | 40 | 186 | 0 | 370 | 40 | 346 | 11 | 0 | 39 | 2 | 47.49 | 0.28 | 170.56 | 0.9989 | 0.5107
26081010801 |  |  |  |  | 1 | 1 | 1 |  | 145 | [6 empty] | 901 | 3 | 1 | 0 | 0 | 0 | 0 | 539 | 2 | 3 | 353 | 27.42 | 0.24 | 114.09 | 0.9994 | 0.2451
26135970300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 78 | 32 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 1 | 0 | 5.06 | 0.04 | 127.31 | 0.9999 | 0.0545
26143970400 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 260 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 200 | 5.77 | 0.08 | 73.06 | 0.9999 | 0.0698
26055550300 |  |  |  |  | 1 | 0.926 |  |  | 0 | [6 empty] | 27 | 13 | 1 | 0 | 0 | 0 | 8 | 1 | 3 | 1 | 0 | 2.27 | 0.01 | 212.04 | 0.9999 | 0.0091
26139024500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 266 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 8.87 | 0.09 | 93.71 | 0.9998 | 0.0111
26049012907 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 338 | 1 | 0.0116
26025002200 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 199 | 0 | 0 | 0 | 0 | 0 | 163 | 36 | 0 | 0 | 0 | 16.53 | 0.13 | 125.69 | 0.9996 | 0.0516
26121002800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 866 | 9 | 0 | 0 | 0 | 0 | 851 | 0 | 2 | 3 | 1 | 25.23 | 0.26 | 98.77 | 0.9994 | 0.1755
26139022002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.19 | 0 | 238 | 1 | 0.0518
26143971200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 119 | 0 | 4.65 | 0.04 | 117.77 | 0.9999 | 0.3405
26081013200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.09 | 0 | 271.6 | 1 | 0.0172
26059051200 |  |  |  |  | 1 | 0.813 |  |  | 211 | [6 empty] | 16 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 2 | 1 | 2.66 | 0.01 | 256.22 | 0.9999 | 0.152
26045021202 |  |  |  |  | 1 | 0.266 |  |  | 0 | [6 empty] | 139 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 108.15 | 0.12 | 934.43 | 0.9975 | 0.1557
26039960200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 50 | 32 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 3.33 | 0.03 | 109.81 | 0.9999 | 0.0515
26121001600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.17 | 0 | 210.99 | 1 | 0.0016
26051000300 |  |  |  |  | 1 | 1 |  |  | 26 | [6 empty] | 251 | 0 | 6 | 0 | 0 | 0 | 244 | 0 | 0 | 1 | 0 | 12.59 | 0.12 | 104.55 | 0.9997 | 0.2068
26155031302 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 35 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.35 | 0 | 646 | 1 | 0.1576
26079950400 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.02 | 0.02 | 46 | 1 | 0.0222
26077005501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.03 | 0 | 53 | 1 | 0.003
26139020200 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 182.73 | 1 | 0.0043
26121000402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0 | 230.11 | 1 | 0.123
26075005700 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.22 | 0 | 177.5 | 1 | 0.0031
26049000700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.51 | 0.01 | 213.8 | 1 | 0.0111
26081001800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0.1 | 0 | 72.71 | 1
26135970202 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 0 | 233.13 | 1 | 0.1723
26081000400 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0.9 | 0.02 | 59.87 | 1 | 0.0852
26121001902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 35 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 2.09 | 0.02 | 126.68 | 1 | 0.097
26075006000 |  |  |  |  | 1 | 1 |  |  | 89 | [6 empty] | 122 | 94 | 0 | 25 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 2.87 | 0.03 | 100.7 | 0.9999 | 0.0515
26065006002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0 | 236.26 | 1 | 0.0084
26127010800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 67 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 66 | 0 | 3.15 | 0.04 | 84.86 | 0.9999 | 0.0127
26077002903 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1.03 | 0 | 211.13 | 1 | 0.0278
26049011302 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 129 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10.84 | 0.08 | 140.62 | 0.9997 | 0.178
26049011010 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 226 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 8.5 | 0.09 | 98.07 | 0.9998 | 0.0065
26025000300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 60 | 1 | 0 | 42 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0.46 | 0.02 | 23.46 | 1 | 0.2108
26081013300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 265 | 0 | 31 | 0 | 0 | 215 | 0 | 19 | 0 | 0 | 0 | 15.55 | 0.15 | 105.22 | 0.9996 | 0.0474
26145011000 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 40 | 1 | 11 | 27 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.88 | 0 | 202.46 | 1 | 0.2161
26145000900 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 14.61 | 0.02 | 909.32 | 0.9997 | 0.0022
26049012310 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 85 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3.24 | 0.06 | 57.93 | 0.9999 | 0.0072
26155031900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.01 | 0 | 12.21 | 1 | 0.0638
26081014200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.1 | 0 | 193 | 1 | 0.001
26009960600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2358 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2355 | 0 | 198.45 | 0.95 | 209.49 | 0.9954 | 0.0285
26137950200 |  |  |  |  | 1 | 1 |  |  | 21 | [6 empty] | 117 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.67 | 0.54 | 212.68 | 0.9973 | 0.106
26005031100 |  |  |  |  | 1 | 0.99 | 1 |  | 0 | [6 empty] | 318 | 2 | 21 | 0 | 0 | 0 | 214 | 61 | 2 | 18 | 0 | 27.41 | 0.09 | 302.45 | 0.9994 | 0.4742
26145012400 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 343 | 42 | 2 | 0 | 0 | 0 | 197 | 57 | 0 | 0 | 45 | 75.61 | 0.4 | 190.69 | 0.9982 | 1.3642
26145012300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 185 | 10 | 0 | 0 | 0 | 0 | 61 | 114 | 0 | 0 | 0 | 21.08 | 0.14 | 155.96 | 0.9995 | 0.2447
26019000400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 0 | 116.16 | 1 | 0.0009
26081012300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 141 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.99 | 0.1 | 192.49 | 0.9996 | 0.007
26121003400 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 32 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 6 | 0 | 1 | 1.71 | 0.02 | 102.28 | 1 | 0.0042
26035000300 |  |  |  |  | 1 | 1 |  |  | 25 | [6 empty] | 425 | 254 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 169 | 0 | 20.57 | 0.15 | 140.71 | 0.9995 | 0.2607
26049011301 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 13 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 3 | 1.58 | 0.01 | 316.07 | 1 | 0.1757
26039960400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 2 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 3.3 | 0.01 | 285.74 | 0.9999 | 0.0596
26005030402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 57 | 1 | 0.0475
26037010400 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 66 | 18 | 30 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 2.85 | 0.04 | 63.86 | 0.9999 | 0.0311
26117970600 |  |  |  |  | 1 | 1 | 1 |  | 18 | [6 empty] | 45 | 12 | 0 | 0 | 0 | 0 | 4 | 28 | 0 | 1 | 0 | 3.6 | 0.02 | 147.71 | 0.9999 | 0.2986
26051000600 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0 | 167.03 | 1 | 0.0486
26081002000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.16 | 0 | 108.75 | 1 | 0.0041
26081001500 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 1 | 0 | 23.24 | 0.25 | 94.31 | 0.9995 | 0.0062
26065005202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 64 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 7.06 | 0.06 | 108.95 | 0.9998 | 0.1083
26005031900 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 6 | 1 | 0 | 0 | 0 | 0.49 | 0 | 166.17 | 1 | 0.0175
26057000900 |  |  |  |  | 1 | 1 | 1 |  | 32 | [6 empty] | 9 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.84 | 0.01 | 142.34 | 1 | 0.1141
26059050200 |  |  |  |  | 1 | 0.983 |  |  | 616 | [6 empty] | 58 | 2 | 0 | 0 | 0 | 0 | 35 | 1 | 0 | 17 | 3 | 2.42 | 0.04 | 64.86 | 0.9999 | 0.1177
26059050100 |  |  |  |  | 1 | 0.99 |  |  | 41 | [6 empty] | 97 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 38 | 4.57 | 0.04 | 129.99 | 0.9999 | 0.0236
26089970400 |  |  |  |  | 1 | 0.996 |  |  | 0 | [6 empty] | 242 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 17.58 | 0.08 | 231.27 | 0.9996 | 0.1464
26121003600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.06 | 0 | 100.25 | 1 | 0.0045
26025000600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 23 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 22 | 1.63 | 0.02 | 85.76 | 1 | 0.0041
26075005302 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 51 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 4 | 0 | 5.65 | 0.03 | 205.18 | 0.9999 | 0.0189
26025002300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 86.37 | 1 | 0.9672
26011970500 |  |  |  |  | 1 | 0.143 | 1 |  | 39 | [6 empty] | 38 | 1 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 30 | 0 | 2.93 | 0.01 | 200.52 | 0.9999 | 0.0477
26077002004 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.06 | 0 | 101.44 | 1 | 0.0022
26081013801 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.24 | 0 | 98.76 | 1 | 0.3511
26107960400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 145 | 42 | 0 | 0 | 0 | 0 | 95 | 0 | 7 | 1 | 0 | 9.07 | 0.09 | 106.38 | 0.9998 | 0.0382
26105950700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 101 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 0 | 16.05 | 0.17 | 94.21 | 0.9996 | 0.0759
26161445000 |  |  |  |  | 1 | 1 |  |  | 428 | [6 empty] | 311 | 3 | 0 | 0 | 0 | 0 | 150 | 149 | 0 | 9 | 0 | 35.03 | 0.23 | 151.29 | 0.9992 | 0.0171
26111290100 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 43 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2.5 | 0.02 | 113.38 | 0.9999 | 0.4357
26049012801 |  |  |  |  | 1 | 0.968 |  |  | 0 | [6 empty] | 124 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 116 | 0 | 14.26 | 0.06 | 227.63 | 0.9997 | 0.0404
26017285201 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 153 | 148 | 3 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 3.3 | 0.05 | 71.74 | 0.9999 | 0.0057
26081002600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 206 | 0 | 0 | 0 | 0 | 0 | 34 | 172 | 0 | 0 | 0 | 20.27 | 0.11 | 181.02 | 0.9995 | 0.0022
26049010502 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | 0 | 1333.06 | 1 | 0.151
26121002700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 19 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 17 | 0 | 0 | 0.62 | 0.01 | 108.47 | 1 | 0.1584
26145011702 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 25 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.09 | 0.02 | 134.19 | 0.9999 | 0.2505
26049011800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0 | 388 | 1 | 0.0035
26081011801 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0.06 | 0 | 125.12 | 1 | 0.0036
26015010800 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 6 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0 | 193 | 1 | 0.3109
26081011403 |  |  |  |  | 1 | 1 |  |  | 11 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.15 | 0 | 202 | 1 | 0.0014
26121001700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 57 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 2.47 | 0.03 | 91.79 | 0.9999 | 0.0005
26081002200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 180 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 6.66 | 0.06 | 108.75 | 0.9998 | 0.0058
26035000500 |  |  |  |  | 1 | 1 |  |  | 91 | [6 empty] | 315 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.3 | 0.18 | 91 | 0.9996 | 0.2047
26045020901 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 160 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 1 | 0.69 | 0.09 | 7.96 | 1 | 0.2941
26081012202 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 467 | 0 | 0 | 457 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0.05 | 0 | 12.65 | 1 | 0.0028
26115833000 |  |  |  |  | 1 | 0.998 |  |  | 13 | [6 empty] | 577 | 375 | 0 | 0 | 0 | 0 | 4 | 187 | 0 | 11 | 0 | 68.43 | 0.25 | 276.82 | 0.9984 | 0.6997
26091062100 |  |  |  |  | 1 | 0.999 | 1 |  | 11 | [6 empty] | 1227 | 1118 | 0 | 0 | 0 | 0 | 21 | 85 | 1 | 2 | 0 | 116.35 | 0.65 | 178.09 | 0.9973 | 0.5027
26121003200 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 397 | 99 | 0 | 46 | 0 | 47 | 205 | 0 | 0 | 0 | 0 | 15.88 | 0.13 | 122.02 | 0.9996 | 0.1368
26111291500 |  |  |  |  | 1 | 1 |  |  | 17 | [6 empty] | 201 | 1 | 0 | 0 | 0 | 5 | 43 | 4 | 0 | 147 | 1 | 11.04 | 0.11 | 102.09 | 0.9997 | 0.1141
26049001500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 340 | 315 | 0 | 23 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 11.11 | 0.56 | 19.83 | 0.9997 | 0.0424
26049010910 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0.3 | 0.03 | 9.87 | 1 | 0.0101
26001000100 |  |  |  |  | 1 | 0.999 |  |  | 7 | [6 empty] | 4450 | 365 | 2 | 0 | 2507 | 0 | 1573 | 0 | 0 | 1 | 2 | 99.89 | 0.76 | 131.87 | 0.9977 | 0.3501
26105950200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 382 | 42 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 21 | 0 | 39.23 | 0.29 | 137.11 | 0.9991 | 0.5386
26005030800 |  |  |  |  | 1 | 0.703 |  |  | 2 | [6 empty] | 172 | 0 | 0 | 0 | 0 | 5 | 150 | 0 | 0 | 10 | 7 | 7.93 | 0.03 | 245.78 | 0.9998 | 0.2166
26091060700 |  |  |  |  | 1 | 0.333 |  |  | 4 | [6 empty] | 3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.7 | 0 | 530.18 | 1 | 0.618
26075006304 |  |  |  |  | 1 | 1 |  |  | 23 | [6 empty] | 170 | 126 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 1 | 0 | 5.47 | 0.09 | 62.03 | 0.9999 | 0.0166
26121003100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 108 | 1 | 0 | 0 | 0 | 0 | 106 | 0 | 1 | 0 | 0 | 6.92 | 0.05 | 126.38 | 0.9998 | 0.065
26049012704 |  |  |  |  | 1 | 0.984 |  |  | 1 | [6 empty] | 62 | 54 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 1 | 1 | 5.66 | 0.03 | 168.67 | 0.9999 | 0.039
26089970600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 276 | 13 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 35.98 | 0.15 | 236.72 | 0.9992 | 1.1261
26049010115 |  |  |  |  | 1 | 1 |  |  | 7 | [6 empty] | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 0.02 | 68.51 | 1 | 0.0114
26037011101 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 89 | 1 | 67 | 1 | 0 | 16 | 0 | 0 | 2 | 2 | 0 | 5.44 | 0.05 | 115.88 | 0.9999 | 0.056
26055551000 |  |  |  |  | 1 | 0.167 |  |  | 0 | [6 empty] | 6 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 12.82 | 0.03 | 499.82 | 0.9997 | 0.9615
26165380800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 66 | 0 | 0 | 0 | 0 | 37 | 0 | 27 | 0 | 0 | 2 | 2.55 | 0.04 | 72.8 | 0.9999 | 0.0191
26081010101 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 187 | 1 | 0 | 0 | 0 | 0 | 157 | 0 | 2 | 27 | 0 | 20.3 | 0.09 | 217.35 | 0.9995 | 0.1059
26121002400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 118 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0.19 | 0 | 70.89 | 1 | 0.0063
26049001300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51 | 0.01 | 67.62 | 1 | 0.0109
26161431000 |  |  |  |  | 1 | 1 | 1 |  | 91 | [6 empty] | 157 | 2 | 0 | 11 | 0 | 0 | 10 | 57 | 0 | 59 | 18 | 5.84 | 0.06 | 100.06 | 0.9999 | 0.4543
26065980000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.03 | 0.02 | 256.02 | 0.9999
26075006702 |  |  |  |  | 1 | 0.9 | 1 |  | 27 | [6 empty] | 328 | 230 | 0 | 0 | 0 | 0 | 3 | 94 | 0 | 1 | 0 | 40.12 | 0.14 | 288.02 | 0.9991 | 0.4238
26115833500 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 34 | 3 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 1 | 0 | 1.9 | 0.01 | 144.41 | 1 | 0.0035
26145002100 |  |  |  |  | 1 | 0.529 | 1 |  | 0 | [6 empty] | 2023 | 1975 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 38 | 0 | 453.89 | 1 | 451.87 | 0.9895 | 1.1038
26145010402 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1208 | 994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 147.78 | 0.41 | 358.06 | 0.9966 | 0.3437
26129950200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 31 | 1 | 22 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 0 | 1.37 | 0.01 | 112.98 | 1 | 0.206
26127010600 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 12 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 0.6 | 0.01 | 65.61 | 1 | 0.0257
26115832200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 440 | 418 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 63.27 | 1.04 | 60.83 | 0.9985 | 0.0236
26037010204 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 46 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.76 | 0.05 | 126.03 | 0.9998 | 0.7666
26023950300 |  |  |  |  | 1 | 1 |  |  | 12 | [6 empty] | 31 | 1 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 1 | 0 | 3.28 | 0.02 | 201.95 | 0.9999 | 0.0031
26081010802 |  |  |  |  | 1 | 1 | 1 |  | 164 | [6 empty] | 771 | 173 | 140 | 0 | 0 | 0 | 66 | 120 | 0 | 272 | 0 | 35.12 | 0.27 | 131.8 | 0.9992 | 0.1355
26133970100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 219 | 9 | 0 | 0 | 0 | 0 | 48 | 0 | 1 | 0 | 161 | 28.46 | 0.18 | 154.25 | 0.9993 | 0.5164
26055550600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 44 | 42 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.43 | 0.02 | 200.89 | 0.9999 | 0.5797
26025002900 |  |  |  |  | 1 | 1 |  |  | 71 | [6 empty] | 27 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 1 | 0 | 4.73 | 0.02 | 255.01 | 0.9999 | 0.0995
26145001900 |  |  |  |  | 1 | 0.072 | 0 |  | 0 | [6 empty] | 489 | 454 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 312.49 | 0.63 | 493.71 | 0.9928 | 1.4955
26045020902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 0 | 0.22 | 0.03 | 6.79 | 1 | 0.515
26137950500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 34 | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 1.96 | 0.02 | 107.15 | 1 | 0.005
26081012500 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 22 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 1.91 | 0.01 | 146.2 | 1 | 0.0006
26139021301 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 30 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0.79 | 0.02 | 32.68 | 1
26049013500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0.47 | 0.01 | 76.04 | 1 | 0.0071
26081014703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0.11 | 0 | 36.46 | 1 | 0.041
26145000100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0 | 89.97 | 1 | 0.0897
26139022108 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 34 | 23 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 3.04 | 0.02 | 159.68 | 0.9999 | 0.0011
26145001100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.15 | 0 | 175.6 | 1 | 0.0083
26069000100 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 556 | 11 | 0 | 349 | 0 | 0 | 171 | 0 | 0 | 0 | 25 | 17.01 | 0.07 | 227.15 | 0.9996 | 0.0604
26037011104 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 1 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 243.8 | 1 | 0.0028
26049011710 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0 | 469 | 1 | 0.0029
26081004200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.16 | 0 | 289.92 | 1 | 0.2845
26149041600 |  |  |  |  | 1 | 0.833 | 1 |  | 279 | [6 empty] | 7 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 2 | 0.89 | 0 | 200.54 | 1 | 0.0216
26073000400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 462 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.76 | 0.24 | 83 | 0.9995 | 0.1999
26145012100 |  |  |  |  | 1 | 0.944 | 1 |  | 0 | [6 empty] | 19 | 5 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 1.53 | 0.01 | 158.14 | 1 | 0.073
26057000100 |  |  |  |  | 1 | 0.995 | 1 |  | 0 | [6 empty] | 183 | 143 | 1 | 0 | 0 | 0 | 38 | 0 | 1 | 0 | 0 | 16.74 | 0.11 | 158.65 | 0.9996 | 0.0611
26025001600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.72 | 0 | 172.33 | 1 | 0.0007
26049012905 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0 | 852 | 1 | 0.0077
26075006200 |  |  |  |  | 1 | 0.993 | 1 |  | 266 | [6 empty] | 137 | 4 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 7.84 | 0.04 | 199.65 | 0.9998 | 0.0138
26075006100 |  |  |  |  | 1 | 1 |  |  | 14 | [6 empty] | 3 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.21 | 0 | 227.47 | 1 | 0.0021
26045020602 |  |  |  |  | 1 | 1 |  |  | 371 | [6 empty] | 90 | 47 | 0 | 0 | 0 | 42 | 0 | 0 | 1 | 0 | 0 | 9.18 | 0.07 | 126.24 | 0.9998 | 0.1672
26045020601 |  |  |  |  | 1 | 1 |  |  | 120 | [6 empty] | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 0 | 144.44 | 1 | 0.0724
26045020302 |  |  |  |  | 1 | 1 |  |  | 5 | [6 empty] | 31 | 1 | 0 | 0 | 0 | 24 | 5 | 0 | 0 | 1 | 0 | 2.02 | 0.01 | 164.65 | 1 | 0.0351
26075006301 |  |  |  |  | 1 | 0.778 |  |  | 132 | [6 empty] | 9 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 1 | 1 | 0 | 1.3 | 0.01 | 232.54 | 1 | 0.3861
26139020100 |  |  |  |  | 1 | 1 | 1 |  | 139 | [6 empty] | 142 | 15 | 0 | 0 | 0 | 0 | 91 | 36 | 0 | 0 | 0 | 13.17 | 0.05 | 239.46 | 0.9997 | 0.763
26155030600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 28 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.08 | 0 | 103 | 1 | 0.7434
26115832600 |  |  |  |  | 1 | 0.172 | 1 |  | 0 | [6 empty] | 30 | 4 | 0 | 0 | 0 | 0 | 25 | 1 | 0 | 0 | 0 | 20.25 | 0.03 | 707.95 | 0.9995 | 0.0105
26025002100 |  |  |  |  | 1 | 1 |  |  | 3 | [6 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 5.03 | 0.04 | 138.64 | 0.9999 | 0.0017
26045021100 |  |  |  |  | 1 | 0.994 | 1 |  | 9 | [6 empty] | 590 | 146 | 233 | 0 | 0 | 64 | 0 | 105 | 0 | 42 | 0 | 33.77 | 0.26 | 130.56 | 0.9992 | 0.0425
26139021500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.8 | 0 | 351.3 | 1 | 0.038
26105950300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 11 | 0 | 0.57 | 0.01 | 94.79 | 1 | 0.2293
26049000900 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 582 | 0 | 0 | 0 | 0 | 387 | 2 | 193 | 0 | 0 | 0 | 72.19 | 0.47 | 152.57 | 0.9983 | 0.0699
26165380400 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 239 | 1 | 57 | 0 | 0 | 165 | 15 | 0 | 0 | 0 | 1 | 5.89 | 0.08 | 71.84 | 0.9999 | 0.2754
26059050400 |  |  |  |  | 1 | 1 |  |  | 767 | [6 empty] | 38 | 5 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 2.73 | 0.01 | 201.03 | 0.9999 | 0.1196
26081011001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 55 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 23 | 5.61 | 0.03 | 172.15 | 0.9999 | 0.1233
26049003700 |  |  |  |  | 1 | 0.797 |  |  | 0 | [6 empty] | 296 | 1 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 77.33 | 0.27 | 287.62 | 0.9982 | 1.1126
26001970100 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1479 | 0 | 2 | 0 | 736 | 0 | 736 | 0 | 0 | 3 | 2 | 47.89 | 0.32 | 151.53 | 0.9989 | 0.194
26023950900 |  |  |  |  | 1 | 1 |  |  | 78 | [6 empty] | 388 | 158 | 0 | 1 | 0 | 0 | 205 | 24 | 0 | 0 | 0 | 36.21 | 0.23 | 160.94 | 0.9992 | 0.0965
26031960600 |  |  |  |  | 1 | 0.993 |  |  | 0 | [6 empty] | 146 | 13 | 0 | 0 | 0 | 0 | 33 | 100 | 0 | 0 | 0 | 17.25 | 0.08 | 215.08 | 0.9996 | 0.106
26125125000 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1.63 | 0 | 701.54 | 1 | 0.0175
26015010402 |  |  |  |  | 1 | 1 | 1 |  | 166 | [6 empty] | 492 | 1 | 356 | 3 | 0 | 0 | 1 | 0 | 0 | 131 | 0 | 33.67 | 0.22 | 152.26 | 0.9992 | 0.2117
26081003900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 5 | 1.08 | 0.01 | 88.89 | 1 | 0.6482
26049002200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 10 | 0 | 0 | 0 | 0 | 9 | 1 | 0 | 0 | 0 | 0 | 1.11 | 0.01 | 78.46 | 1 | 0.3177
26065006100 |  |  |  |  | 1 | 1 | 1 |  | 5 | [6 empty] | 63 | 61 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 10.34 | 0.03 | 321.47 | 0.9998 | 0.0026
26081011902 |  |  |  |  | 1 | 0.995 | 1 |  | 1 | [6 empty] | 1325 | 157 | 0 | 1103 | 0 | 0 | 0 | 1 | 64 | 0 | 0 | 10.25 | 0.07 | 152.56 | 0.9998 | 0.003
26105950100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.64 | 0 | 308 | 1 | 0.0042
26085961100 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 96 | 1 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 3 | 0 | 17.1 | 0.06 | 282.46 | 0.9996 | 0.1299
26111291700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 521 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 194 | 0 | 14.72 | 0.23 | 64.97 | 0.9997 | 0.0222
26091060100 |  |  |  |  | 1 | 1 |  |  | 722 | [6 empty] | 446 | 2 | 0 | 442 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.64 | 0 | 185.7 | 1 | 0.1159
26055550700 |  |  |  |  | 1 | 0.5 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0.44 | 0 | 451 | 1 | 1.1119
26067031700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 1 | 0 | 2.7 | 0.04 | 73.68 | 0.9999 | 0.3365
26049012100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 48 | 1 | 0.0141
26025001100 |  |  |  |  | 1 | 0.717 |  |  | 0 | [6 empty] | 544 | 0 | 0 | 0 | 0 | 544 | 0 | 0 | 0 | 0 | 0 | 61.05 | 0.25 | 249.03 | 0.9986 | 0.639
26145011200 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 38 | 28 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 5 | 1 | 7.57 | 0.04 | 184.71 | 0.9998 | 0.1316
26029001400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.04 | 0 | 40 | 1 | 0.0105
26031960300 |  |  |  |  | 1 | 0.882 |  |  | 0 | [6 empty] | 17 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 15 | 0.61 | 0.01 | 72.78 | 1 | 0.0025
26121001000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.09 | 0 | 83.28 | 1 | 0.0011
26075005301 |  |  |  |  | 1 | 1 |  |  | 2 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 0.2161
26139022105 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.18 | 0 | 161.77 | 1 | 0.0011
26139022106 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0 | 170.85 | 1 | 0.0008
26139021400 |  |  |  |  | 1 | 0.995 | 1 |  | 1 | [6 empty] | 680 | 5 | 0 | 77 | 0 | 364 | 182 | 0 | 5 | 1 | 46 | 26.83 | 0.15 | 177.15 | 0.9994 | 0.0678
26049013002 |  |  |  |  | 1 | 0.833 |  |  | 0 | [6 empty] | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 0 | 265.75 | 1 | 0.0017
26121001901 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 43 | 22 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 2.94 | 0.02 | 119.34 | 0.9999 | 0.0528
26077001000 |  |  |  |  | 1 | 0.999 | 1 |  | 4 | [6 empty] | 957 | 0 | 911 | 44 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 32.73 | 0.33 | 98.68 | 0.9992 | 0.2139
26069000800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 29.5 | 0.13 | 224.15 | 0.9993 | 0.5431
26107960800 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 118 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 0 | 25.41 | 0.11 | 240.57 | 0.9994 | 0.4611
26001970500 |  |  |  |  | 1 | 0.958 | 1 |  | 0 | [6 empty] | 803 | 37 | 3 | 0 | 560 | 0 | 200 | 0 | 0 | 3 | 0 | 10.13 | 0.08 | 125.79 | 0.9998 | 0.2961
26075005500 |  |  |  |  | 1 | 1 | 1 |  | 1 | [6 empty] | 18 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 2 | 4 | 1.62 | 0.01 | 299.1 | 1 | 0.521
26129950100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 14 | 11 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1.56 | 0.01 | 245.53 | 1 | 0.0847
26139021606 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 2 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | 471.59 | 1 | 0.0042
26049002800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 238 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.58 | 0.14 | 18.6 | 0.9999 | 0.0111
26077003004 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 184 | 0 | 0 | 0 | 0 | 111 | 0 | 10 | 0 | 0 | 63 | 5.27 | 0.06 | 92.48 | 0.9999 | 0.0034
26065005002 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.38 | 0 | 282.39 | 1
26005030600 |  |  |  |  | 1 | 0.952 | 1 |  | 0 | [6 empty] | 42 | 3 | 3 | 0 | 0 | 0 | 34 | 2 | 0 | 0 | 0 | 8.29 | 0.02 | 424.58 | 0.9998 | 0.3787
26145010200 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 59.66 | 1 | 0.5291
26049003200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.38 | 0 | 427.08 | 1 | 0.0674
26117971000 |  |  |  |  | 1 | 1 | 1 |  | 2 | [6 empty] | 40 | 19 | 2 | 0 | 0 | 0 | 2 | 8 | 1 | 8 | 0 | 2.29 | 0.02 | 126.69 | 0.9999 | 0.2739
26145000800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.77 | 0 | 281.86 | 1 | 0.7147
26077002002 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0.25 | 0 | 128.81 | 1 | 0.0043
26145012500 |  |  |  |  | 1 | 0.917 | 1 |  | 0 | [6 empty] | 14 | 1 | 1 | 0 | 0 | 0 | 5 | 4 | 0 | 2 | 1 | 1.95 | 0.01 | 268.82 | 1 | 1.1919
26049010812 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 221 | 61 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 7.97 | 0.11 | 70.69 | 0.9998 | 0.2443
26049002900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0.36 | 0.07 | 5.34 | 1 | 0.0256
26049010911 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 0 | 279.42 | 1 | 3.4367
26011970200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 32 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.76 | 0.01 | 130.21 | 1 | 1.1091
26051000900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 24 | 6 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 1.04 | 0.01 | 79.34 | 1 | 0.2456
26081002100 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1012 | 0 | 0 | 0 | 0 | 0 | 979 | 33 | 0 | 0 | 0 | 60.89 | 0.53 | 115.89 | 0.9986 | 0.5312
26081001000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 21 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0.01 | 241.91 | 0.9999 | 0.1518
26015010401 |  |  |  |  | 1 | 1 | 1 |  | 139 | [6 empty] | 257 | 0 | 0 | 20 | 0 | 0 | 234 | 0 | 0 | 2 | 1 | 45.14 | 0.14 | 329.48 | 0.999 | 0.1439
26077001501 |  |  |  |  | 1 | 1 | 1 |  | 12 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.05 | 0 | 51.5 | 1 | 0.0147
26051000400 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 615 | 25 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 586 | 18.91 | 0.31 | 61.95 | 0.9996 | 0.1417
26023951100 |  |  |  |  | 1 | 1 |  |  | 920 | [6 empty] | 2179 | 0 | 0 | 1726 | 0 | 443 | 10 | 0 | 0 | 0 | 0 | 36.94 | 0.2 | 181.09 | 0.9991 | 0.253
26049012603 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 169 | 58 | 0 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 0 | 24.16 | 0.13 | 180.83 | 0.9994 | 0.1534
26055550900 |  |  |  |  | 1 | 0.953 | 1 |  | 0 | [6 empty] | 65 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 1 | 1 | 0 | 4.8 | 0.02 | 246.56 | 0.9999 | 1.1075
26065004500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 1.21 | 0.01 | 200.29 | 1 | 0.208
26005031200 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 23 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 0 | 15 | 0 | 1.93 | 0.01 | 243.77 | 1 | 0.6198
26005031000 |  |  |  |  | 1 | 0.849 | 1 |  | 199 | [6 empty] | 521 | 14 | 0 | 124 | 0 | 0 | 332 | 1 | 0 | 0 | 50 | 31.95 | 0.12 | 271.81 | 0.9993 | 0.5902
26111291102 |  |  |  |  | 1 | 0.366 |  |  | 2642 | [6 empty] | 2691 | 0 | 0 | 2650 | 0 | 0 | 27 | 0 | 0 | 1 | 13 | 4.42 | 0.01 | 518.48 | 0.9999 | 0.1022
26101000600 |  |  |  |  | 1 | 1 |  |  | 21 | [6 empty] | 242 | 0 | 1 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 1 | 17.77 | 0.17 | 103.69 | 0.9996 | 0.488
26135970500 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 172 | 2 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 1 | 0 | 19.56 | 0.1 | 192.84 | 0.9995 | 0.0542
26093710700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 2.67 | 0.02 | 109.03 | 0.9999 | 0.0144
26139023002 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 545 | 371 | 11 | 53 | 0 | 0 | 109 | 0 | 0 | 1 | 0 | 31.49 | 0.24 | 129.86 | 0.9993 | 0.104
26077000300 |  |  |  |  | 1 |  | 1 |  | 1 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0.96 | 0.01 | 122.3 | 1 | 0.0157
26051000800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0.43 | 0.01 | 81.31 | 1 | 0.0178
26045021401 |  |  |  |  | 1 | 1 | 1 |  | 30 | [6 empty] | 72 | 53 | 8 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 6.78 | 0.05 | 124.7 | 0.9998 | 0.0211
26111290200 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 12 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 1.32 | 0 | 300.12 | 1 | 0.9824
26145001000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0.7 | 0.01 | 47.23 | 1 | 0.2202
26023951600 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.39 | 0 | 112.97 | 1
26007000100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 75 | 0 | 0 | 0 | 74 | 0 | 1 | 0 | 0 | 0 | 0 | 1.89 | 0.01 | 151.44 | 1 | 0.1875
26081001700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 571 | 1 | 0 | 5 | 0 | 0 | 0 | 565 | 0 | 0 | 0 | 27.53 | 0.29 | 94.79 | 0.9994 | 0.0108
26123970900 |  |  |  |  | 1 | 1 | 1 |  | 189 | [6 empty] | 295 | 1 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 40 | 0 | 13.44 | 0.14 | 94.96 | 0.9997 | 0.4578
26025003300 |  |  |  |  | 1 | 1 | 1 |  | 35 | [6 empty] | 45 | 2 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 7.44 | 0.05 | 158.49 | 0.9998 | 0.0574
26121002100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.03 | 0 | 63.39 | 1
26049012008 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0.01 | 56.54 | 1 | 0.0015
26049011714 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 32 | 1 | 0 | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.16 | 0 | 124.24 | 1 | 0.0052
26067030400 |  |  |  |  | 1 | 1 | 1 |  | 557 | [6 empty] | 1691 | 43 | 88 | 1313 | 0 | 1 | 58 | 0 | 2 | 186 | 0 | 7.37 | 0.11 | 64.85 | 0.9998 | 0.1373
26081001102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0.01 | 137.56 | 1
26143970500 |  |  |  |  | 1 | 0.845 | 1 |  | 0 | [6 empty] | 1077 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 1019 | 27.22 | 0.48 | 56.34 | 0.9994 | 0.5882
26017286300 |  |  |  |  | 1 | 0.988 | 1 |  | 8 | [6 empty] | 87 | 21 | 0 | 0 | 0 | 0 | 58 | 0 | 1 | 6 | 1 | 8.07 | 0.04 | 192.28 | 0.9998 | 0.0135
26129950900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.07 | 0 | 102 | 1 | 0.8943
26143971100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 344 | 11 | 1 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 21.18 | 0.13 | 168.18 | 0.9995 | 0.6878
26113960200 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 44 | 0 | 1 | 0 | 0 | 0 | 0 | 13 | 0 | 30 | 0 | 2.64 | 0.02 | 172.62 | 0.9999 | 0.0351
26069000700 |  |  |  |  | 1 | 0.714 |  |  | 0 | [6 empty] | 7 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 1.62 | 0 | 458.4 | 1 | 0.1121
26049012802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 41 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.08 | 0.05 | 321.02 | 0.9997
26145011100 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 12 | 0 | 2.71 | 0.01 | 190.2 | 0.9999 | 0.1998
26025002600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.06 | 0 | 58.1 | 1 | 0.013
26139022206 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0.48 | 0 | 142.44 | 1
26023950800 |  |  |  |  | 1 | 1 | 1 |  | 366 | [6 empty] | 385 | 88 | 0 | 188 | 0 | 0 | 89 | 19 | 0 | 1 | 0 | 18.14 | 0.12 | 156.89 | 0.9996 | 0.2001
26015010200 |  |  |  |  | 1 | 1 | 1 |  | 31 | [6 empty] | 222 | 75 | 0 | 0 | 0 | 28 | 56 | 0 | 62 | 1 | 0 | 11.87 | 0.11 | 111.31 | 0.9997 | 0.1383
26079950200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.38 | 0 | 150.58 | 1 | 0.26
26049010112 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 0 | 303 | 1 | 0.0017
26149041300 |  |  |  |  | 1 | 1 |  |  | 12 | [6 empty] | 25 | 3 | 1 | 0 | 0 | 1 | 4 | 0 | 0 | 16 | 0 | 0.98 | 0.01 | 148.95 | 1 | 0.0471
26005030300 |  |  |  |  | 1 | 1 | 0.961 |  | 20 | [6 empty] | 840 | 329 | 26 | 0 | 0 | 0 | 348 | 134 | 1 | 2 | 0 | 52.54 | 0.3 | 177.46 | 0.9988 | 0.0254
26149041500 |  |  |  |  | 1 | 1 |  |  | 6 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.24 | 0 | 85.83 | 1 | 0.3597
26057000800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 1.13 | 0.01 | 119.25 | 1 | 0.0075
26121003700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0 | 167.03 | 1 | 0.0029
26077002202 |  |  |  |  | 1 | 1 |  |  | 54 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.39 | 0 | 205.24 | 1 | 0.0038
26017286000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.69 | 0 | 389.85 | 1 | 0.0035
26081004400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0.15 | 0 | 55.35 | 1 | 0.001
26155031700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 382 | 0 | 0 | 364 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0.95 | 0.01 | 111.82 | 1 | 0.3193
26123971100 |  |  |  |  | 1 | 1 | 1 |  | 9 | [6 empty] | 324 | 23 | 1 | 0 | 0 | 0 | 299 | 0 | 0 | 1 | 0 | 15.72 | 0.13 | 118.43 | 0.9996 | 0.0197
26077001701 |  |  |  |  | 1 | 1 |  |  | 1 | [6 empty] | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 0.01 | 110 | 1 | 0.6792
26141950200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 117 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.41 | 0.07 | 164.77 | 0.9997 | 0.0012
26049001400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 356 | 266 | 0 | 0 | 0 | 89 | 1 | 0 | 0 | 0 | 0 | 39.24 | 0.58 | 67.91 | 0.9991 | 0.2451
26139021605 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.89 | 0 | 320.29 | 1 | 0.0007
26121002500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 758 | 94 | 0 | 610 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 5.17 | 0.04 | 122.72 | 0.9999 | 0.0139
26145012003 |  |  |  |  | 1 | 0.983 |  |  | 0 | [6 empty] | 58 | 54 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 5.37 | 0.02 | 236.1 | 0.9999 | 0.0815
26035000600 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 36 | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 0.02 | 109.09 | 1 | 0.0288
26081014805 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1183 | 0 | 0 | 0 | 0 | 0 | 0 | 1082 | 97 | 4 | 0 | 48.93 | 0.37 | 132.39 | 0.9989 | 0.518
26025002400 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 64 | 1 | 0 | 0 | 0 | 0 | 54 | 7 | 2 | 0 | 0 | 11.28 | 0.05 | 235.13 | 0.9997 | 0.7084
26139020501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87 | 0 | 237.81 | 1 | 0.0005
26047970600 |  |  |  |  | 1 | 0.492 |  |  | 0 | [6 empty] | 61 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 442.88 | 1.24 | 355.76 | 0.9897 | 0.4898
26065004801 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 10 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0.49 | 0 | 125.24 | 1 | 0.0373
26081011405 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 26 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 2.47 | 0.02 | 127.25 | 0.9999
26005030704 |  |  |  |  | 1 | 0.994 |  |  | 1 | [6 empty] | 1132 | 0 | 7 | 0 | 0 | 0 | 1125 | 0 | 0 | 0 | 0 | 108.72 | 0.53 | 204.39 | 0.9975 | 0.0052
26067031900 |  |  |  |  | 1 | 1 | 1 |  | 45 | [6 empty] | 160 | 21 | 1 | 45 | 0 | 0 | 41 | 5 | 0 | 46 | 1 | 5.51 | 0.04 | 132.56 | 0.9999 | 0.3226
26067031300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 177 | 3 | 2 | 0 | 0 | 58 | 113 | 0 | 0 | 1 | 0 | 7.09 | 0.05 | 153.23 | 0.9998 | 0.0868
26077001506 |  |  |  |  | 1 | 0.542 |  |  | 0 | [6 empty] | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.31 | 0.01 | 375.03 | 0.9999 | 0.3485
26145010303 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 18 | 7 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 2.08 | 0.01 | 184.43 | 1 | 0.1222
26105950800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 22 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 1.1 | 0.02 | 67.25 | 1 | 0.0141
26049011211 |  |  |  |  | 1 | 0 |  |  | 3 | [6 empty] | 9 | 0 | 0 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.18 | 0 | 531.64 | 1 | 0.0076
26019000200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 574 | 0 | 1 | 0 | 0 | 0 | 571 | 1 | 1 | 0 | 0 | 46.62 | 0.25 | 184.36 | 0.9989 | 0.2401
26081012800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 86 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 2.21 | 0.05 | 45.71 | 0.9999
26059051100 |  |  |  |  | 1 | 0.735 | 1 |  | 164 | [6 empty] | 440 | 113 | 0 | 0 | 0 | 1 | 173 | 26 | 0 | 61 | 66 | 67.16 | 0.2 | 340.09 | 0.9984 | 0.5224
26081012703 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.04 | 0 | 32.78 | 1 | 0.1628
26067031500 |  |  |  |  | 1 | 0.6 | 1 |  | 0 | [6 empty] | 20 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 6 | 0.04 | 140.14 | 0.9999
26049010503 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 121 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.79 | 0.12 | 161.07 | 0.9995 | 0.0335
26025002000 |  |  |  |  | 1 | 1 |  |  | 48 | [6 empty] | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 1.71 | 0.01 | 214.36 | 1 | 0.0052
26145011300 |  |  |  |  | 1 | 0.273 |  |  | 0 | [6 empty] | 15 | 1 | 0 | 4 | 0 | 0 | 0 | 8 | 1 | 1 | 0 | 1.26 | 0 | 441.04 | 1 | 0.0316
26025003700 |  |  |  |  | 1 | 0.202 | 1 |  | 23 | [6 empty] | 458 | 154 | 0 | 0 | 0 | 8 | 0 | 281 | 0 | 15 | 0 | 100.56 | 0.18 | 545.6 | 0.9977 | 0.0221
26139022900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 9 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 3 | 4 | 6.28 | 0.05 | 126.36 | 0.9999
26073000300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 71 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 3.82 | 0.07 | 54.61 | 0.9999 | 0.067
26155031401 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 59 | 10 | 46 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 9.06 | 0.02 | 438.32 | 0.9998 | 0.5985
26111291601 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0 | 153 | 1 | 0.1589
26145001600 |  |  |  |  | 1 | 0.727 |  |  | 0 | [6 empty] | 55 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.96 | 0.03 | 407.41 | 0.9997 | 1.9246
26023951300 |  |  |  |  | 1 | 1 | 1 |  | 21 | [6 empty] | 58 | 0 | 0 | 8 | 0 | 0 | 4 | 12 | 0 | 0 | 34 | 4.35 | 0.05 | 92.76 | 0.9999 | 0.1612
26017285600 |  |  |  |  | 1 | 1 | 1 |  | 16 | [6 empty] | 28 | 7 | 0 | 16 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 0.47 | 0 | 145.88 | 1 | 0.1509
26049003100 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.57 | 0.01 | 627.46 | 0.9999 | 0.0233
26113960400 |  |  |  |  | 1 | 0.957 |  |  | 0 | [6 empty] | 46 | 0 | 1 | 0 | 0 | 0 | 44 | 1 | 0 | 0 | 0 | 1.14 | 0.02 | 46.71 | 1 | 0.0856
26035001300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 230 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 6 | 9.22 | 0.07 | 132.19 | 0.9998 | 0.0297
26139024300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.37 | 0 | 448.28 | 1 | 0.0095
26037010300 |  |  |  |  | 1 | 1 |  |  | 25 | [6 empty] | 32 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 28 | 0 | 1.41 | 0.01 | 109.15 | 1 | 0.4479
26081014501 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 1.22 | 0.02 | 79.85 | 1 | 0.0041
26129950300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 689 | 0 | 0 | 0 | 0 | 0 | 689 | 0 | 0 | 0 | 0 | 29.86 | 0.28 | 107.59 | 0.9993 | 1.0854
26073940100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 82.18 | 1 | 0.0404
26117971300 |  |  |  |  | 1 | 1 |  |  | 84 | [6 empty] | 200 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 92 | 0 | 8.63 | 0.07 | 127.82 | 0.9998 | 0.0479
26081010600 |  |  |  |  | 1 | 1 | 1 |  | 38 | [6 empty] | 1313 | 12 | 371 | 0 | 0 | 0 | 165 | 259 | 1 | 15 | 490 | 22.33 | 0.25 | 90.48 | 0.9995 | 0.9005
26009960500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 94 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 93 | 0 | 12.02 | 0.06 | 211.39 | 0.9997
26081010700 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 122 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.88 | 0.05 | 104.13 | 0.9999 | 0.0061
26081011401 |  |  |  |  | 1 | 1 | 1 |  | 23 | [6 empty] | 46 | 2 | 0 | 0 | 0 | 0 | 2 | 6 | 1 | 0 | 35 | 4.83 | 0.04 | 136.5 | 0.9999 | 0.053
26143970300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 123 | 15 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 11.06 | 0.06 | 181.03 | 0.9997 | 0.1212
26121001200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 7 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 0.52 | 0 | 113.78 | 1 | 0.0055
26137950100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.09 | 0.01 | 13.83 | 1 | 0.3067
26045021001 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 70 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0.26 | 0.04 | 6.87 | 1 | 0.0027
26077002700 |  |  |  |  | 1 | 1 | 1 |  | 249 | [6 empty] | 249 | 41 | 0 | 0 | 0 | 152 | 52 | 2 | 0 | 1 | 1 | 15.11 | 0.06 | 250.69 | 0.9997 | 0.0179
26107960900 |  |  |  |  | 1 | 0.909 |  |  | 1 | [6 empty] | 23 | 2 | 0 | 1 | 0 | 0 | 2 | 2 | 0 | 16 | 0 | 1.64 | 0.01 | 179.25 | 1 | 0.2752
26075005200 |  |  |  |  | 1 | 1 |  |  | 57 | [6 empty] | 32 | 10 | 0 | 13 | 0 | 1 | 8 | 0 | 0 | 0 | 0 | 0.84 | 0.01 | 129.31 | 1 | 0.0031
26091061800 |  |  |  |  | 1 | 1 | 1 |  | 7 | [6 empty] | 133 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 11.28 | 0.07 | 163.63 | 0.9997 | 0.0664
26077000900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 9.85 | 0.06 | 172.63 | 0.9998 | 0.0025
26025003800 |  |  |  |  | 1 | 1 | 1 |  | 396 | [6 empty] | 69 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 25 | 1.91 | 0.03 | 57.42 | 1 | 0.1274
26139021902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 324 | 0 | 0 | 277 | 0 | 43 | 0 | 0 | 4 | 0 | 0 | 10.29 | 0.03 | 387.92 | 0.9998 | 0.0503
26129950600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 118 | 0 | 97 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 10.24 | 0.06 | 177.17 | 0.9998 | 1.3038
26093732100 |  |  |  |  | 1 | 1 |  |  | 4 | [6 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0.73 | 0 | 151.84 | 1 | 0.006
26077001300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 34 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 3.46 | 0.03 | 101.63 | 0.9999 | 0.001
26081012902 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 738 | 0 | 40 | 0.31 | 127.25 | 0.9991 | 0.1789
26075005400 |  |  |  |  | 1 | 1 | 1 |  | 92 | [6 empty] | 81 | 30 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 1 | 9.85 | 0.03 | 314.4 | 0.9998 | 0.1323
26111291200 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1317 | 86 | 0 | 0 | 0 | 1050 | 138 | 0 | 0 | 37 | 6 | 30.48 | 0.5 | 60.48 | 0.9993 | 0.4669
26077002101 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.03 | 0 | 113 | 1 | 0.0014
26115831800 |  |  |  |  | 1 | 0 |  |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 112.7 | 0.1 | 1127.02 | 0.9974 | 0.0333
26139022203 |  |  |  |  | 1 | 0.992 |  |  | 0 | [6 empty] | 128 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 1 | 0 | 21.12 | 0.17 | 127.53 | 0.9995 | 0.0026
26073000800 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0.01 | 83 | 1 | 0.0617
26159010200 |  |  |  |  | 1 | 0.997 | 1 |  | 429 | [6 empty] | 1063 | 2 | 268 | 306 | 0 | 0 | 484 | 0 | 0 | 2 | 1 | 64.46 | 0.31 | 210.73 | 0.9985 | 0.2384
26121002000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1 | 0 | 0.45 | 0.01 | 62.36 | 1 | 0.0391
26011970300 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.09 | 0 | 133.53 | 1 | 0.0189
26129950400 |  |  |  |  | 1 | 0.988 | 1 |  | 0 | [6 empty] | 320 | 3 | 316 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 10.76 | 0.11 | 99.17 | 0.9998 | 0.7291
26049011401 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.16 | 0 | 304 | 1 | 0.0027
26017285202 |  |  |  |  | 1 | 0.664 |  |  | 46 | [6 empty] | 140 | 46 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 47 | 46 | 20.84 | 0.08 | 266.19 | 0.9995 | 0.8781
26081013700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 1136 | 0 | 1075 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 18.18 | 0.33 | 55.2 | 0.9996 | 0.0029
26111290500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 161 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 16 | 0 | 65.6 | 0.19 | 350.02 | 0.9985 | 0.078
26081011702 |  |  |  |  | 1 | 0.667 |  |  | 0 | [6 empty] | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0.45 | 0 | 365.05 | 1 | 0.0521
26117970100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 39 | 1 | 0.0083
26101000900 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 139 | 1 | 0.0017
26037010802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 323.52 | 1 | 0.0705
26065004302 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 69.99 | 1
26081011500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.08 | 0 | 306 | 1 | 0.0167
26145012600 |  |  |  |  | 1 | 0.998 | 1 |  | 0 | [6 empty] | 510 | 1 | 1 | 0 | 0 | 0 | 493 | 11 | 0 | 0 | 4 | 40.6 | 0.3 | 136.92 | 0.9991 | 1.268
26049011505 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.41 | 0 | 270.27 | 1 | 0.0008
26025002800 |  |  |  |  | 1 | 0.968 | 1 |  | 175 | [6 empty] | 32 | 29 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 1.9 | 0.01 | 130.17 | 1 | 0.107
26015010700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 54 | 0 | 13 | 37 | 0 | 0 | 1 | 1 | 2 | 0 | 0 | 0.93 | 0.01 | 135.24 | 1 | 0.1631
26077006701 |  |  |  |  | 1 | 1 |  |  | 207 | [6 empty] | 136 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 15.84 | 0.11 | 149.45 | 0.9996 | 0.0857
26039960100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 31 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 17.09 | 0.11 | 159.34 | 0.9996 | 0.7543
26049011102 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 149 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.94 | 0.05 | 453.41 | 0.9995 | 0.0016
26051000200 |  |  |  |  | 1 | 1 |  |  | 5 | [6 empty] | 161 | 6 | 102 | 1 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 11.36 | 0.08 | 141.2 | 0.9997 | 0.8129
26017285700 |  |  |  |  | 1 | 0.2 |  |  | 0 | [6 empty] | 5 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 1.36 | 0 | 510.04 | 1 | 0.0144
26121004000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.21 | 0 | 238.23 | 1 | 0.0585
26049001200 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 93 | 16 | 0 | 0 | 0 | 72 | 0 | 5 | 0 | 0 | 0 | 14.13 | 0.08 | 175.3 | 0.9997 | 0.0511
26121001402 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 47 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0.68 | 0.01 | 59.45 | 1 | 0.0432
26081011901 |  |  |  |  | 1 | 0.984 | 1 |  | 38 | [6 empty] | 548 | 2 | 3 | 475 | 0 | 0 | 35 | 30 | 0 | 1 | 2 | 6.55 | 0.03 | 251.87 | 0.9998 | 0.1043
26049012503 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 22 | 1 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 2.8 | 0.02 | 164.7 | 0.9999 | 0.1451
26091062300 |  |  |  |  | 1 | 1 |  |  | 118 | [6 empty] | 221 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.12 | 0.09 | 102.36 | 0.9998 | 0.0975
26037011001 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 32 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 28 | 2.15 | 0.02 | 111.49 | 1 | 0.0482
26037011002 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 31 | 0 | 29 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1.78 | 0.02 | 86.63 | 1 | 0.1547
26005032000 |  |  |  |  | 1 | 1 | 1 |  | 10 | [6 empty] | 376 | 0 | 0 | 0 | 0 | 0 | 281 | 95 | 0 | 0 | 0 | 41.37 | 0.16 | 262.65 | 0.999 | 0.2618
26055550500 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1.53 | 0.01 | 172.65 | 1 | 0.0356
26139021100 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 17 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1.02 | 0.01 | 166.1 | 1 | 0.0029
26065003802 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 77 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 75 | 87.43 | 0.2 | 439.42 | 0.998 | 0.0646
26065003901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 56 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 73.31 | 0.37 | 200.29 | 0.9983 | 0.1634
26073940600 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 59 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 1 | 0 | 2.06 | 0.03 | 66.28 | 1 | 0.1117
26025001900 |  |  |  |  | 1 | 1 | 1 |  | 4 | [6 empty] | 133 | 0 | 0 | 0 | 0 | 0 | 67 | 66 | 0 | 0 | 0 | 12.98 | 0.06 | 200.59 | 0.9997 | 0.0029
26065005600 |  |  |  |  | 1 | 1 |  |  | 136 | [6 empty] | 11 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0.3 | 0 | 61.74 | 1 | 0.1155
26081012605 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0.35 | 0 | 134.33 | 1 | 0.0094
26149041000 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 215 | 0 | 213 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 14.19 | 0.11 | 126.16 | 0.9997 | 0.0335
26039960300 |  |  |  |  | 1 |  | 1 |  | 0 | [6 empty] | 29 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 1.22 | 0.02 | 59.28 | 1 | 0.1986
26017285300 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.08 | 0 | 88.76 | 1 | 0.0307
26155030400 |  |  |  |  | 1 | 0 | 1 |  | 0 | [6 empty] | 6 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.03 | 0 | 456.76 | 1 | 0.7186
26049010305 |  |  |  |  | 1 | 0.667 |  |  | 0 | [6 empty] | 3 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.38 | 0 | 237.29 | 1 | 0.0053
26025003400 |  |  |  |  | 1 | 1 |  |  | 111 | [6 empty] | 114 | 96 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 14.25 | 0.13 | 112.99 | 0.9997 | 0.1372
26009960700 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 245 | 1 | 241 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 27.27 | 0.17 | 163.29 | 0.9994 | 0.7907
26065004901 |  |  |  |  | 1 | 1 |  |  | 0 | [6 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 69 | 1 | 0.0356
26005030902 |  |  |  |  | 1 | 0.958 | 1 |  | 0 | [6 empty] | 142 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 21.16 | 0.07 | 297.89 | 0.9995 | 0.4207
26055550800 |  |  |  |  | 1 | 1 | 1 |  | 0 | [6 empty] | 214 | 205 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17.2 | 0.16 | 107.07 | 0.9996 | 1.2402
MPSC Annual Performance Standard | 95% or more | 90% or more completed within 15 business days | 90% or more within 120 minutes in MSAs | 90% or more within 180 minutes in non-MSAs | 90% or more customers restored in 36 hours or less | 90% or more customers restored in 8 hours or less | 90% or more customers restored in 24 hours or less | 90% or more customers restored in 48 hours or less | 6% or less before 2030; 5% or less in 2030 or later

## SourceData
Utility_Name | Reporting Periods | Storm Type | Year Picker
Alpena Power Co. | 2024-03-31 | Wind | 2024-06-30
Citizens Gas Fuel Co. | 2024-02-29 | Ice | 2023-06-30
Consumers Energy Co. | 2024-01-31 | Rain | 2022-06-30
DTE Energy Co. | 2023-12-31 | Thunderstorm | 2021-06-30
Indiana Michigan Power Co. | 2023-11-30 | Snow | 2020-06-30
Michigan Gas Utilities | 2023-10-31 | Combination | 2019-06-30
Northern States Power Co. (Xcel) | 2023-09-30 |  | 2018-06-30
Semco Energy Gas Co. | 2023-08-31 |  | 2017-06-30
Upper Michigan Energy Resources | 2023-07-31 |  | 2016-06-30
Upper Peninsula Power Co. | 2023-06-30 |  | 2015-06-30
Z-Test-Utility | 2023-05-31 |  | 2014-06-30
| 2023-04-30 |  | 2013-06-30
| 2023-03-31 |  | 2012-06-30
| 2023-02-28 |  | 2011-06-30
| 2023-01-31 |  | 2010-06-30
| 2022-11-30 |  | 2009-06-30
| 2022-12-31 |  | 2008-06-30
| 2022-10-31 |  | 2007-06-30
| 2022-09-30 |  | 2006-06-30
2005-06-30
2004-06-30
2003-06-30
2002-06-30
2001-06-30
2000-06-30
1999-06-30
1998-06-30
1997-06-30
1996-06-30
1995-06-30
1994-06-30
1993-06-30
1992-06-30
1991-06-30
1990-06-30
1989-06-30
1988-06-30
1987-06-30
1986-06-30
1985-06-30
1984-06-30
1983-06-30
1982-06-30
1981-06-30
1980-06-30
1979-06-30
1978-06-30
1977-06-30
1976-06-30
1975-06-30
1974-06-30
Formulas:
Year Picker = DATE(YEAR([Year Picker, row above])-1, 6, 30)

## NormalizedData
Title | Utility | Reporting_Period | Cred_96_R_N | Cred_96_C_N | Cred_96_I_N | Cred_48_R_N | Cred_48_C_N | Cred_48_I_N | Cred_16_R_N | Cred_16_C_N | Cred_16_I_N | Cred_6_R_N | Cred_6_C_N | Cred_6_I_N | Cred_96_R_Dol | Cred_96_C_Dol | Cred_96_I_Dol | Cred_48_R_Dol | Cred_48_C_Dol | Cred_48_I_Dol | Cred_16_R_Dol | Cred_16_C_Dol | Cred_16_I_Dol | Cred_6_R_Dol | Cred_6_C_Dol | Cred_6_I_Dol | CEMI1_M | CEMI1_YTD | CEMI2_M | CEMI2_YTD | CEMI3_M | CEMI3_YTD | CEMI4_M | CEMI4_YTD | CEMI5_M | CEMI5_YTD | CEMI6_M | CEMI6_YTD | CEMI7_M | CEMI7_YTD | CEMI8_M | CEMI8_YTD | CEMI9_M | CEMI9_YTD | CEMI10_M | CEMI10_YTD | CELID8hours | CELID24hours | CELID48hours | CELID_MI | S1_Name | S1_DB | S1_DE | S1_Type | S1_NCI | S1_SD | S1_RED | S1_RE_DE | S1_M_Spent | S1_M_OC | S1_NBRR | S1_NCL | S1_NConW | S1_NBW | S1_NCC | S1_NConC | S1_NBC | S1_NWD | S1_DW | S1_NBRC | S2_Name | S2_DB | S2_DE | S2_Type | S2_NCI | S2_SD | S2_RED | S2_RE_DE | S2_M_Spent | S2_M_OC | S2_NBRR | S2_NCL | S2_NConW | S2_NBW | S2_NCC | S2_NConC | S2_NBC | S2_NWD | S2_DW | S2_NBRC | S3_Name | S3_DB | S3_DE | S3_Type | S3_NCI | S3_SD | S3_RED | S3_RE_DE | S3_M_Spent | S3_M_OC | S3_NBRR | S3_NCL | S3_NConW | S3_NBW | S3_NCC | S3_NConC | S3_NBC | S3_NWD | S3_DW | S3_NBRC | S4_Name | S4_DB | S4_DE | S4_Type | S4_NCI | S4_SD | S4_RED | S4_RE_DE | S4_M_Spent | S4_M_OC | S4_NBRR | S4_NCL | S4_NConW | S4_NBW | S4_NCC | S4_NConC | S4_NBC | S4_NWD | S4_DW | S4_NBRC | S5_Name | S5_DB | S5_DE | S5_Type | S5_NCI | S5_SD | S5_RED | S5_RE_DE | S5_M_Spent | S5_M_OC | S5_NBRR | S5_NCL | S5_NConW | S5_NBW | S5_NCC | S5_NConC | S5_NBC | S5_NWD | S5_DW | S5_NBRC
U-21122 Response Data | Consumers Energy Co. | 45046 | 67 | 2 | 0 | 0 | 0 | 0 | 562 | 69 | 2 | 16 | 1 | 0 | 1675 | 6.96 | 0 | 0 | 0 | 0 | 19350 | 50.28 | 10.06 | 450 | 35 | 0 | 150219 | 620641 | 14494 | 207776 | 1758 | 75241 | 8 | 29662 | 0 | 10770 | 0 | 3493 | 0 | 1086 | 0 | 520 | 0 | 314 | 0 | 63 | 9341 | 137 | 0 | 28278 |  | 45017 |  |  | 10247 |  | 22 | 45017 | 1502519 | [10 empty] | 304071 |  | 45021 |  |  | 27116 |  | 14 | 45021 | 2147193 | [10 empty] | 507500
Title | Utility | Reporting_Period | Cred_96_R_N | Cred_96_C_N | Cred_96_I_N | Cred_48_R_N | Cred_48_C_N | Cred_48_I_N | Cred_16_R_N | Cred_16_C_N | Cred_16_I_N | Cred_6_R_N | Cred_6_C_N | Cred_6_I_N | Cred_96_R_Dol | Cred_96_C_Dol | Cred_96_I_Dol | Cred_48_R_Dol | Cred_48_C_Dol | Cred_48_I_Dol | Cred_16_R_Dol | Cred_16_C_Dol | Cred_16_I_Dol | Cred_6_R_Dol | Cred_6_C_Dol | Cred_6_I_Dol | CEMI1_M | CEMI1_YTD | CEMI2_M | CEMI2_YTD | CEMI3_M | CEMI3_YTD | CEMI4_M | CEMI4_YTD | CEMI5_M | CEMI5_YTD | CEMI6_M | CEMI6_YTD | CEMI7_M | CEMI7_YTD | CEMI8_M | CEMI8_YTD | CEMI9_M | CEMI9_YTD | CEMI10_M | CEMI10_YTD | CELID8hours | CELID24hours | CELID48hours | CELID_MI | S1_Name | S1_DB | S1_DE | S1_Type | S1_NCI | S1_SD | S1_RED | S1_RE_DE | S1_M_Spent | S1_M_OC | S1_NBRR | S1_NCL | S1_NConW | S1_NBW | S1_NCC | S1_NConC | S1_NBC | S1_NWD | S1_DW | S1_NBRC | S2_Name | S2_DB | S2_DE | S2_Type | S2_NCI | S2_SD | S2_RED | S2_RE_DE | S2_M_Spent | S2_M_OC | S2_NBRR | S2_NCL | S2_NConW | S2_NBW | S2_NCC | S2_NConC | S2_NBC | S2_NWD | S2_DW | S2_NBRC | S3_Name | S3_DB | S3_DE | S3_Type | S3_NCI | S3_SD | S3_RED | S3_RE_DE | S3_M_Spent | S3_M_OC | S3_NBRR | S3_NCL | S3_NConW | S3_NBW | S3_NCC | S3_NConC | S3_NBC | S3_NWD | S3_DW | S3_NBRC | S4_Name | S4_DB | S4_DE | S4_Type | S4_NCI | S4_SD | S4_RED | S4_RE_DE | S4_M_Spent | S4_M_OC | S4_NBRR | S4_NCL | S4_NConW | S4_NBW | S4_NCC | S4_NConC | S4_NBC | S4_NWD | S4_DW | S4_NBRC | S5_Name | S5_DB | S5_DE | S5_Type | S5_NCI | S5_SD | S5_RED | S5_RE_DE | S5_M_Spent | S5_M_OC | S5_NBRR | S5_NCL | S5_NConW | S5_NBW | S5_NCC | S5_NConC | S5_NBC | S5_NWD | S5_DW | S5_NBRC
Linked | Consumers Energy Co. | 2023-04-30 | 67 | 2 | 0 | 0 | 0 | 0 | 562 | 69 | 2 | 16 | 1 | 0 | 1675 | 6.96 | 0 | 0 | 0 | 0 | 19350 | 50.28 | 10.06 | 450 | 35 | 0 | 150219 | 620641 | 14494 | 207776 | 1758 | 75241 | 8 | 29662 | 0 | 10770 | 0 | 3493 | 0 | 1086 | 0 | 520 | 0 | 314 | 0 | 63 | 9341 | 137 | 0 | 28278 | 0 | 2023-04-01 | 0 | 0 | 10247 | 0 | 22 | 2023-04-01 | 1502519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304071 | 0 | 2023-04-05 | 0 | 0 | 27116 | 0 | 14 | 2023-04-05 | 2147193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static | Credits, worst circuits, storms'!C3 | Credits, worst circuits, storms'!C4 | Credits, worst circuits, storms'!E8 | Credits, worst circuits, storms'!E9 | Credits, worst circuits, storms'!E10 | Credits, worst circuits, storms'!E11 | Credits, worst circuits, storms'!E12 | Credits, worst circuits, storms'!E13 | Credits, worst circuits, storms'!E14 | Credits, worst circuits, storms'!E15 | Credits, worst circuits, storms'!E16 | Credits, worst circuits, storms'!E17 | Credits, worst circuits, storms'!E18 | Credits, worst circuits, storms'!E19 | Credits, worst circuits, storms'!F8 | Credits, worst circuits, storms'!F9 | Credits, worst circuits, storms'!F10 | Credits, worst circuits, storms'!F11 | Credits, worst circuits, storms'!F12 | Credits, worst circuits, storms'!F13 | Credits, worst circuits, storms'!F14 | Credits, worst circuits, storms'!F15 | Credits, worst circuits, storms'!F16 | Credits, worst circuits, storms'!F17 | Credits, worst circuits, storms'!F18 | Credits, worst circuits, storms'!F19 | Credits, worst circuits, storms'!D60 | Credits, worst circuits, storms'!D61 | Credits, worst circuits, storms'!E60 | Credits, worst circuits, storms'!E61 | Credits, worst circuits, storms'!F60 | Credits, worst circuits, storms'!F61 | Credits, worst circuits, storms'!G60 | Credits, worst circuits, storms'!G61 | Credits, worst circuits, storms'!H60 | Credits, worst circuits, storms'!H61 | Credits, worst circuits, storms'!I60 | Credits, worst circuits, storms'!I61 | Credits, worst circuits, storms'!J60 | Credits, worst circuits, storms'!J61 | Credits, worst circuits, storms'!K60 | Credits, worst circuits, storms'!K61 | Credits, worst circuits, storms'!L60 | Credits, worst circuits, storms'!L61 | Credits, worst circuits, storms'!M60 | Credits, worst circuits, storms'!M61 | Credits, worst circuits, storms'!D63 | Credits, worst circuits, storms'!D64 | Credits, worst circuits, storms'!D65 | Credits, worst circuits, storms'!D66 | Credits, worst circuits, storms'!C69 | Credits, worst circuits, storms'!C70 | Credits, worst circuits, storms'!C71 | Credits, worst circuits, storms'!C72 | Credits, worst circuits, storms'!C73 | Credits, worst circuits, storms'!C74 | Credits, worst circuits, storms'!C75 | Credits, worst circuits, storms'!C76 | Credits, worst circuits, storms'!C77 | Credits, worst circuits, storms'!C78 | Credits, worst circuits, storms'!C79 | Credits, worst circuits, storms'!C80 | Credits, worst circuits, storms'!C81 | Credits, worst circuits, storms'!C82 | Credits, worst circuits, storms'!C83 | Credits, worst circuits, storms'!C84 | Credits, worst circuits, storms'!C85 | Credits, worst circuits, storms'!C86 | Credits, worst circuits, storms'!C87 | Credits, worst circuits, storms'!C88 | Credits, worst circuits, storms'!D69 | Credits, worst circuits, storms'!D70 | Credits, worst circuits, storms'!D71 | Credits, worst circuits, storms'!D72 | Credits, worst circuits, storms'!D73 | Credits, worst circuits, storms'!D74 | Credits, worst circuits, storms'!D75 | Credits, worst circuits, storms'!D76 | Credits, worst circuits, storms'!D77 | Credits, worst circuits, storms'!D78 | Credits, worst circuits, storms'!D79 | Credits, worst circuits, storms'!D80 | Credits, worst circuits, storms'!D81 | Credits, worst circuits, storms'!D82 | Credits, worst circuits, storms'!D83 | Credits, worst circuits, storms'!D84 | Credits, worst circuits, storms'!D85 | Credits, worst circuits, storms'!D86 | Credits, worst circuits, storms'!D87 | Credits, worst circuits, storms'!D88 | Credits, worst circuits, storms'!E69 | Credits, worst circuits, storms'!E70 | Credits, worst circuits, storms'!E71 | Credits, worst circuits, storms'!E72 | Credits, worst circuits, storms'!E73 | Credits, worst circuits, storms'!E74 | Credits, worst circuits, storms'!E75 | Credits, worst circuits, storms'!E76 | Credits, worst circuits, storms'!E77 | Credits, worst circuits, storms'!E78 | Credits, worst circuits, storms'!E79 | Credits, worst circuits, storms'!E80 | Credits, worst circuits, storms'!E81 | Credits, worst circuits, storms'!E82 | Credits, worst circuits, storms'!E83 | Credits, worst circuits, storms'!E84 | Credits, worst circuits, storms'!E85 | Credits, worst circuits, storms'!E86 | Credits, worst circuits, storms'!E87 | Credits, worst circuits, storms'!E88 | Credits, worst circuits, storms'!F69 | Credits, worst circuits, storms'!F70 | Credits, worst circuits, storms'!F71 | Credits, worst circuits, storms'!F72 | Credits, worst circuits, storms'!F73 | Credits, worst circuits, storms'!F74 | Credits, worst circuits, storms'!F75 | Credits, worst circuits, storms'!F76 | Credits, worst circuits, storms'!F77 | Credits, worst circuits, storms'!F78 | Credits, worst circuits, storms'!F79 | Credits, worst circuits, storms'!F80 | Credits, worst circuits, storms'!F81 | Credits, worst circuits, storms'!F82 | Credits, worst circuits, storms'!F83 | Credits, worst circuits, storms'!F84 | Credits, worst circuits, storms'!F85 | Credits, worst circuits, storms'!F86 | Credits, worst circuits, storms'!F87 | Credits, worst circuits, storms'!F88 | Credits, worst circuits, storms'!G69 | Credits, worst circuits, storms'!G70 | Credits, worst circuits, storms'!G71 | Credits, worst circuits, storms'!G72 | Credits, worst circuits, storms'!G73 | Credits, worst circuits, storms'!G74 | Credits, worst circuits, storms'!G75 | Credits, worst circuits, storms'!G76 | Credits, worst circuits, storms'!G77 | Credits, worst circuits, storms'!G78 | Credits, worst circuits, storms'!G79 | Credits, worst circuits, storms'!G80 | Credits, worst circuits, storms'!G81 | Credits, worst circuits, storms'!G82 | Credits, worst circuits, storms'!G83 | Credits, worst circuits, storms'!G84 | Credits, worst circuits, storms'!G85 | Credits, worst circuits, storms'!G86 | Credits, worst circuits, storms'!G87 | Credits, worst circuits, storms'!G88
Title | Utility | Reporting_Period | C1_SAIDI_I-A | C1_SAIDI_CName | C1_SAIDI_CNum | C1_SAIDI_MCL | C1_SAIDI_M_W_R | C1_SAIDI_M_W_C | C1_SAIDI_M_W_I | C1_SAIDI_M_W_O | C1_SAIDI_A_ExMED_R | C1_SAIDI_A_ExMED_C | C1_SAIDI_A_ExMED_I | C1_SAIDI_A_ExMED_O | C1_SAIDI_CS_R | C1_SAIDI_CS_C | C1_SAIDI_CS_I | C1_SAIDI_Sub_Name | C1_SAIDI_S_ZC | C1_SAIDI_S_CT | C1_SAIDI_LCT | C1_SAIDI_LOC | C2_SAIDI_I-A | C2_SAIDI_CName | C2_SAIDI_CNum | C2_SAIDI_MCL | C2_SAIDI_M_W_R | C2_SAIDI_M_W_C | C2_SAIDI_M_W_I | C2_SAIDI_M_W_O | C2_SAIDI_A_ExMED_R | C2_SAIDI_A_ExMED_C | C2_SAIDI_A_ExMED_I | C2_SAIDI_A_ExMED_O | C2_SAIDI_CS_R | C2_SAIDI_CS_C | C2_SAIDI_CS_I | C2_SAIDI_Sub_Name | C2_SAIDI_S_ZC | C2_SAIDI_S_CT | C2_SAIDI_LCT | C2_SAIDI_LOC | C3_SAIDI_I-A | C3_SAIDI_CName | C3_SAIDI_CNum | C3_SAIDI_MCL | C3_SAIDI_M_W_R | C3_SAIDI_M_W_C | C3_SAIDI_M_W_I | C3_SAIDI_M_W_O | C3_SAIDI_A_ExMED_R | C3_SAIDI_A_ExMED_C | C3_SAIDI_A_ExMED_I | C3_SAIDI_A_ExMED_O | C3_SAIDI_CS_R | C3_SAIDI_CS_C | C3_SAIDI_CS_I | C3_SAIDI_Sub_Name | C3_SAIDI_S_ZC | C3_SAIDI_S_CT | C3_SAIDI_LCT | C3_SAIDI_LOC | C4_SAIDI_I-A | C4_SAIDI_CName | C4_SAIDI_CNum | C4_SAIDI_MCL | C4_SAIDI_M_W_R | C4_SAIDI_M_W_C | C4_SAIDI_M_W_I | C4_SAIDI_M_W_O | C4_SAIDI_A_ExMED_R | C4_SAIDI_A_ExMED_C | C4_SAIDI_A_ExMED_I | C4_SAIDI_A_ExMED_O | C4_SAIDI_CS_R | C4_SAIDI_CS_C | C4_SAIDI_CS_I | C4_SAIDI_Sub_Name | C4_SAIDI_S_ZC | C4_SAIDI_S_CT | C4_SAIDI_LCT | C4_SAIDI_LOC | C5_SAIDI_I-A | C5_SAIDI_CName | C5_SAIDI_CNum | C5_SAIDI_MCL | C5_SAIDI_M_W_R | C5_SAIDI_M_W_C | C5_SAIDI_M_W_I | C5_SAIDI_M_W_O | C5_SAIDI_A_ExMED_R | C5_SAIDI_A_ExMED_C | C5_SAIDI_A_ExMED_I | C5_SAIDI_A_ExMED_O | C5_SAIDI_CS_R | C5_SAIDI_CS_C | C5_SAIDI_CS_I | C5_SAIDI_Sub_Name | C5_SAIDI_S_ZC | C5_SAIDI_S_CT | C5_SAIDI_LCT | C5_SAIDI_LOC | C6_SAIDI_I-A | C6_SAIDI_CName | C6_SAIDI_CNum | C6_SAIDI_MCL | C6_SAIDI_M_W_R | C6_SAIDI_M_W_C | C6_SAIDI_M_W_I | C6_SAIDI_M_W_O | C6_SAIDI_A_ExMED_R | C6_SAIDI_A_ExMED_C | C6_SAIDI_A_ExMED_I | C6_SAIDI_A_ExMED_O | C6_SAIDI_CS_R | C6_SAIDI_CS_C | C6_SAIDI_CS_I | C6_SAIDI_Sub_Name | C6_SAIDI_S_ZC | C6_SAIDI_S_CT | C6_SAIDI_LCT | C6_SAIDI_LOC | C7_SAIDI_I-A | C7_SAIDI_CName | C7_SAIDI_CNum | C7_SAIDI_MCL | C7_SAIDI_M_W_R | C7_SAIDI_M_W_C | C7_SAIDI_M_W_I | C7_SAIDI_M_W_O | C7_SAIDI_A_ExMED_R | C7_SAIDI_A_ExMED_C | C7_SAIDI_A_ExMED_I | C7_SAIDI_A_ExMED_O | C7_SAIDI_CS_R | C7_SAIDI_CS_C | C7_SAIDI_CS_I | C7_SAIDI_Sub_Name | C7_SAIDI_S_ZC | C7_SAIDI_S_CT | C7_SAIDI_LCT | C7_SAIDI_LOC | C8_SAIDI_I-A | C8_SAIDI_CName | C8_SAIDI_CNum | C8_SAIDI_MCL | C8_SAIDI_M_W_R | C8_SAIDI_M_W_C | C8_SAIDI_M_W_I | C8_SAIDI_M_W_O | C8_SAIDI_A_ExMED_R | C8_SAIDI_A_ExMED_C | C8_SAIDI_A_ExMED_I | C8_SAIDI_A_ExMED_O | C8_SAIDI_CS_R | C8_SAIDI_CS_C | C8_SAIDI_CS_I | C8_SAIDI_Sub_Name | C8_SAIDI_S_ZC | C8_SAIDI_S_CT | C8_SAIDI_LCT | C8_SAIDI_LOC | C9_SAIDI_I-A | C9_SAIDI_CName | C9_SAIDI_CNum | C9_SAIDI_MCL | C9_SAIDI_M_W_R | C9_SAIDI_M_W_C | C9_SAIDI_M_W_I | C9_SAIDI_M_W_O | C9_SAIDI_A_ExMED_R | C9_SAIDI_A_ExMED_C | C9_SAIDI_A_ExMED_I | C9_SAIDI_A_ExMED_O | C9_SAIDI_CS_R | C9_SAIDI_CS_C | C9_SAIDI_CS_I | C9_SAIDI_Sub_Name | C9_SAIDI_S_ZC | C9_SAIDI_S_CT | C9_SAIDI_LCT | C9_SAIDI_LOC | C10_SAIDI_I-A | C10_SAIDI_CName | C10_SAIDI_CNum | C10_SAIDI_MCL | C10_SAIDI_M_W_R | C10_SAIDI_M_W_C | C10_SAIDI_M_W_I | C10_SAIDI_M_W_O | C10_SAIDI_A_ExMED_R | C10_SAIDI_A_ExMED_C | C10_SAIDI_A_ExMED_I | C10_SAIDI_A_ExMED_O | C10_SAIDI_CS_R | C10_SAIDI_CS_C | C10_SAIDI_CS_I | C10_SAIDI_Sub_Name | C10_SAIDI_S_ZC | C10_SAIDI_S_CT | C10_SAIDI_LCT | C10_SAIDI_LOC
U-21122 Response Data | Consumers Energy Co. | 45046 | circuit1 | SPRINGPORT | 54201 | 78.94 | 1090.19351 | 162.73241 | 0 | 1268.29906 |  |  |  |  | 775 | 114 | 0 | SPRINGPORT | 48827, 49224, 49269, 49284 | 26025003200, 26025003700, 26045021100, 26045021202, 26075006500, 26075006600 | 42551 | Equipment Failure-99.6%, Public Tree Trimming-0.2%, No Specific Cause Found-0.2% | circuit2 | DEVEREAUX | 54202 | 43.86 | 1079.63695 | 145.41176 | 4.40642 | 1236.06476 |  |  |  |  | 569 | 73 | 2 | SPRINGPORT | 48827, 49284 | 26045021202, 26075006600 | 40724 | Equipment Failure-100.0% | circuit3 | STATE STREET | 21703 | 9.58 | 484.49124 | 36.14751 | 0 | 524.75311 |  |  |  |  | 1893 | 127 | 0 | STATE STREET | 48602, 48603 | 26145001500, 26145001600, 26145002000, 26145002100, 26145010401 | 42916 | Equipment Failure-98.6%, Trees-1.4% | circuit4 | HOSPITAL | 72301 | 5.06 | 497.42264 | 20.78526 | 0 | 524.29658 |  |  |  |  | 1068 | 40 | 0 | BARNARD | 48602 | 26145001800, 26145001900, 26145002000, 26145010401 | 44012 | Equipment Failure-99.9%, Weather-0.1% | circuit5 | WEISS | 72302 | 8.98 | 485.15056 | 32.12354 | 0 | 521.05334 |  |  |  |  | 1506 | 95 | 0 | BARNARD | 48602, 48603 | 26145001900, 26145002000, 26145002100, 26145010401, 26145010700 | 45107 | Equipment Failure-99.8%, No Specific Cause Found-0.2% | circuit6 | BARNARD | 72304 | 11.37 | 370.2474 | 146.07943 | 0 | 519.69271 |  |  |  |  | 624 | 239 | 0 | BARNARD | 48603 | 26145010304, 26145010401 | 41820 | Equipment Failure-100.0% | circuit7 | BAYSIDE | 72303 | 11.12 | 337.36441 | 175.98446 | 2.9209 | 517.73023 |  |  |  |  | 525 | 268 | 6 | BARNARD | 48603 | 26145010304, 26145010401 | 41820 | Equipment Failure-100.0% | circuit8 | WARWICK | 21702 | 10.96 | 390.2058 | 23.58551 | 0 | 414.08986 |  |  |  |  | 1440 | 94 | 0 | STATE STREET | 48602, 48603 | 26145002100, 26145010401, 26145010402 | 41455 | Equipment Failure-100.0% | circuit9 | MACKINAW | 21701 | 9.32 | 379.96247 | 20.95536 | 0 | 403.00796 |  |  |  |  | 1640 | 91 | 0 | STATE STREET | 48602, 48603, 48638 | 26145001500, 26145002100, 26145010402 | 44377 | Equipment Failure-100.0% | circuit10 | ELK RAPIDS | 79802 | 26.24 | 319.11428 | 79.86831 | 0.28245 | 401.52391 |  |  |  |  | 1234 | 322 | 1 | ANTRIM | 49629, 49648, 49690 | 26009960600 | 42551 | No Specific Cause Found-100.0%, Equipment Failure-0.0%
Title | Utility | Reporting_Period | C1_SAIDI_I-A | C1_SAIDI_CName | C1_SAIDI_CNum | C1_SAIDI_MCL | C1_SAIDI_M_W_R | C1_SAIDI_M_W_C | C1_SAIDI_M_W_I | C1_SAIDI_M_W_O | C1_SAIDI_A_ExMED_R | C1_SAIDI_A_ExMED_C | C1_SAIDI_A_ExMED_I | C1_SAIDI_A_ExMED_O | C1_SAIDI_CS_R | C1_SAIDI_CS_C | C1_SAIDI_CS_I | C1_SAIDI_Sub_Name | C1_SAIDI_S_ZC | C1_SAIDI_S_CT | C1_SAIDI_LCT | C1_SAIDI_LOC | C2_SAIDI_I-A | C2_SAIDI_CName | C2_SAIDI_CNum | C2_SAIDI_MCL | C2_SAIDI_M_W_R | C2_SAIDI_M_W_C | C2_SAIDI_M_W_I | C2_SAIDI_M_W_O | C2_SAIDI_A_ExMED_R | C2_SAIDI_A_ExMED_C | C2_SAIDI_A_ExMED_I | C2_SAIDI_A_ExMED_O | C2_SAIDI_CS_R | C2_SAIDI_CS_C | C2_SAIDI_CS_I | C2_SAIDI_Sub_Name | C2_SAIDI_S_ZC | C2_SAIDI_S_CT | C2_SAIDI_LCT | C2_SAIDI_LOC | C3_SAIDI_I-A | C3_SAIDI_CName | C3_SAIDI_CNum | C3_SAIDI_MCL | C3_SAIDI_M_W_R | C3_SAIDI_M_W_C | C3_SAIDI_M_W_I | C3_SAIDI_M_W_O | C3_SAIDI_A_ExMED_R | C3_SAIDI_A_ExMED_C | C3_SAIDI_A_ExMED_I | C3_SAIDI_A_ExMED_O | C3_SAIDI_CS_R | C3_SAIDI_CS_C | C3_SAIDI_CS_I | C3_SAIDI_Sub_Name | C3_SAIDI_S_ZC | C3_SAIDI_S_CT | C3_SAIDI_LCT | C3_SAIDI_LOC | C4_SAIDI_I-A | C4_SAIDI_CName | C4_SAIDI_CNum | C4_SAIDI_MCL | C4_SAIDI_M_W_R | C4_SAIDI_M_W_C | C4_SAIDI_M_W_I | C4_SAIDI_M_W_O | C4_SAIDI_A_ExMED_R | C4_SAIDI_A_ExMED_C | C4_SAIDI_A_ExMED_I | C4_SAIDI_A_ExMED_O | C4_SAIDI_CS_R | C4_SAIDI_CS_C | C4_SAIDI_CS_I | C4_SAIDI_Sub_Name | C4_SAIDI_S_ZC | C4_SAIDI_S_CT | C4_SAIDI_LCT | C4_SAIDI_LOC | C5_SAIDI_I-A | C5_SAIDI_CName | C5_SAIDI_CNum | C5_SAIDI_MCL | C5_SAIDI_M_W_R | C5_SAIDI_M_W_C | C5_SAIDI_M_W_I | C5_SAIDI_M_W_O | C5_SAIDI_A_ExMED_R | C5_SAIDI_A_ExMED_C | C5_SAIDI_A_ExMED_I | C5_SAIDI_A_ExMED_O | C5_SAIDI_CS_R | C5_SAIDI_CS_C | C5_SAIDI_CS_I | C5_SAIDI_Sub_Name | C5_SAIDI_S_ZC | C5_SAIDI_S_CT | C5_SAIDI_LCT | C5_SAIDI_LOC | C6_SAIDI_I-A | C6_SAIDI_CName | C6_SAIDI_CNum | C6_SAIDI_MCL | C6_SAIDI_M_W_R | C6_SAIDI_M_W_C | C6_SAIDI_M_W_I | C6_SAIDI_M_W_O | C6_SAIDI_A_ExMED_R | C6_SAIDI_A_ExMED_C | C6_SAIDI_A_ExMED_I | C6_SAIDI_A_ExMED_O | C6_SAIDI_CS_R | C6_SAIDI_CS_C | C6_SAIDI_CS_I | C6_SAIDI_Sub_Name | C6_SAIDI_S_ZC | C6_SAIDI_S_CT | C6_SAIDI_LCT | C6_SAIDI_LOC | C7_SAIDI_I-A | C7_SAIDI_CName | C7_SAIDI_CNum | C7_SAIDI_MCL | C7_SAIDI_M_W_R | C7_SAIDI_M_W_C | C7_SAIDI_M_W_I | C7_SAIDI_M_W_O | C7_SAIDI_A_ExMED_R | C7_SAIDI_A_ExMED_C | C7_SAIDI_A_ExMED_I | C7_SAIDI_A_ExMED_O | C7_SAIDI_CS_R | C7_SAIDI_CS_C | C7_SAIDI_CS_I | C7_SAIDI_Sub_Name | C7_SAIDI_S_ZC | C7_SAIDI_S_CT | C7_SAIDI_LCT | C7_SAIDI_LOC | C8_SAIDI_I-A | C8_SAIDI_CName | C8_SAIDI_CNum | C8_SAIDI_MCL | C8_SAIDI_M_W_R | C8_SAIDI_M_W_C | C8_SAIDI_M_W_I | C8_SAIDI_M_W_O | C8_SAIDI_A_ExMED_R | C8_SAIDI_A_ExMED_C | C8_SAIDI_A_ExMED_I | C8_SAIDI_A_ExMED_O | C8_SAIDI_CS_R | C8_SAIDI_CS_C | C8_SAIDI_CS_I | C8_SAIDI_Sub_Name | C8_SAIDI_S_ZC | C8_SAIDI_S_CT | C8_SAIDI_LCT | C8_SAIDI_LOC | C9_SAIDI_I-A | C9_SAIDI_CName | C9_SAIDI_CNum | C9_SAIDI_MCL | C9_SAIDI_M_W_R | C9_SAIDI_M_W_C | C9_SAIDI_M_W_I | C9_SAIDI_M_W_O | C9_SAIDI_A_ExMED_R | C9_SAIDI_A_ExMED_C | C9_SAIDI_A_ExMED_I | C9_SAIDI_A_ExMED_O | C9_SAIDI_CS_R | C9_SAIDI_CS_C | C9_SAIDI_CS_I | C9_SAIDI_Sub_Name | C9_SAIDI_S_ZC | C9_SAIDI_S_CT | C9_SAIDI_LCT | C9_SAIDI_LOC | C10_SAIDI_I-A | C10_SAIDI_CName | C10_SAIDI_CNum | C10_SAIDI_MCL | C10_SAIDI_M_W_R | C10_SAIDI_M_W_C | C10_SAIDI_M_W_I | C10_SAIDI_M_W_O | C10_SAIDI_A_ExMED_R | C10_SAIDI_A_ExMED_C | C10_SAIDI_A_ExMED_I | C10_SAIDI_A_ExMED_O | C10_SAIDI_CS_R | C10_SAIDI_CS_C | C10_SAIDI_CS_I | C10_SAIDI_Sub_Name | C10_SAIDI_S_ZC | C10_SAIDI_S_CT | C10_SAIDI_LCT | C10_SAIDI_LOC
Linked | Consumers Energy Co. | 2023-04-30 | circuit1 | SPRINGPORT | 54201 | 78.94 | 1090.1935 | 162.7324 | 0 | 1268.2991 | #REF! | #REF! | #REF! | #REF! | 775 | 114 | 0 | SPRINGPORT | 48827, 49224, 49269, 49284 | 26025003200, 26025003700, 26045021100, 26045021202, 26075006500, 26075006600 | 2016-06-30 | Equipment Failure-99.6%, Public Tree Trimming-0.2%, No Specific Cause Found-0.2% | circuit2 | DEVEREAUX | 54202 | 43.86 | 1079.637 | 145.4118 | 4.4064 | 1236.0648 | #REF! | #REF! | #REF! | #REF! | 569 | 73 | 2 | SPRINGPORT | 48827, 49284 | 26045021202, 26075006600 | 2011-06-30 | Equipment Failure-100.0% | circuit3 | STATE STREET | 21703 | 9.58 | 484.4912 | 36.1475 | 0 | 524.7531 | #REF! | #REF! | #REF! | #REF! | 1893 | 127 | 0 | STATE STREET | 48602, 48603 | 26145001500, 26145001600, 26145002000, 26145002100, 26145010401 | 2017-06-30 | Equipment Failure-98.6%, Trees-1.4% | circuit4 | HOSPITAL | 72301 | 5.06 | 497.4226 | 20.7853 | 0 | 524.2966 | #REF! | #REF! | #REF! | #REF! | 1068 | 40 | 0 | BARNARD | 48602 | 26145001800, 26145001900, 26145002000, 26145010401 | 2020-06-30 | Equipment Failure-99.9%, Weather-0.1% | circuit5 | WEISS | 72302 | 8.98 | 485.1506 | 32.1235 | 0 | 521.0533 | #REF! | #REF! | #REF! | #REF! | 1506 | 95 | 0 | BARNARD | 48602, 48603 | 26145001900, 26145002000, 26145002100, 26145010401, 26145010700 | 2023-06-30 | Equipment Failure-99.8%, No Specific Cause Found-0.2% | circuit6 | BARNARD | 72304 | 11.37 | 370.2474 | 146.0794 | 0 | 519.6927 | #REF! | #REF! | #REF! | #REF! | 624 | 239 | 0 | BARNARD | 48603 | 26145010304, 26145010401 | 2014-06-30 | Equipment Failure-100.0% | circuit7 | BAYSIDE | 72303 | 11.12 | 337.3644 | 175.9845 | 2.9209 | 517.7302 | #REF! | #REF! | #REF! | #REF! | 525 | 268 | 6 | BARNARD | 48603 | 26145010304, 26145010401 | 2014-06-30 | Equipment Failure-100.0% | circuit8 | WARWICK | 21702 | 10.96 | 390.2058 | 23.5855 | 0 | 414.0899 | #REF! | #REF! | #REF! | #REF! | 1440 | 94 | 0 | STATE STREET | 48602, 48603 | 26145002100, 26145010401, 26145010402 | 2013-06-30 | Equipment Failure-100.0% | circuit9 | MACKINAW | 21701 | 9.32 | 379.9625 | 20.9554 | 0 | 403.008 | #REF! | #REF! | #REF! | #REF! | 1640 | 91 | 0 | STATE STREET | 48602, 48603, 48638 | 26145001500, 26145002100, 26145010402 | 2021-06-30 | Equipment Failure-100.0% | circuit10 | ELK RAPIDS | 79802 | 26.24 | 319.1143 | 79.8683 | 0.28245 | 401.5239 | #REF! | #REF! | #REF! | #REF! | 1234 | 322 | 1 | ANTRIM | 49629, 49648, 49690 | 26009960600 | 2016-06-30 | No Specific Cause Found-100.0%, Equipment Failure-0.0%
Static | Credits, worst circuits, storms'!C3 | Credits, worst circuits, storms'!C4 | Credits, worst circuits, storms'!D25 | Credits, worst circuits, storms'!D26 | Credits, worst circuits, storms'!D27 | Credits, worst circuits, storms'!D28 | Credits, worst circuits, storms'!D29 | Credits, worst circuits, storms'!D30 | Credits, worst circuits, storms'!D31 | Credits, worst circuits, storms'!D32 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!D33 | Credits, worst circuits, storms'!D34 | Credits, worst circuits, storms'!D35 | Credits, worst circuits, storms'!D36 | Credits, worst circuits, storms'!D37 | Credits, worst circuits, storms'!D38 | Credits, worst circuits, storms'!D39 | Credits, worst circuits, storms'!D40 | Credits, worst circuits, storms'!E25 | Credits, worst circuits, storms'!E26 | Credits, worst circuits, storms'!E27 | Credits, worst circuits, storms'!E28 | Credits, worst circuits, storms'!E29 | Credits, worst circuits, storms'!E30 | Credits, worst circuits, storms'!E31 | Credits, worst circuits, storms'!E32 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!E33 | Credits, worst circuits, storms'!E34 | Credits, worst circuits, storms'!E35 | Credits, worst circuits, storms'!E36 | Credits, worst circuits, storms'!E37 | Credits, worst circuits, storms'!E38 | Credits, worst circuits, storms'!E39 | Credits, worst circuits, storms'!E40 | Credits, worst circuits, storms'!F25 | Credits, worst circuits, storms'!F26 | Credits, worst circuits, storms'!F27 | Credits, worst circuits, storms'!F28 | Credits, worst circuits, storms'!F29 | Credits, worst circuits, storms'!F30 | Credits, worst circuits, storms'!F31 | Credits, worst circuits, storms'!F32 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!F33 | Credits, worst circuits, storms'!F34 | Credits, worst circuits, storms'!F35 | Credits, worst circuits, storms'!F36 | Credits, worst circuits, storms'!F37 | Credits, worst circuits, storms'!F38 | Credits, worst circuits, storms'!F39 | Credits, worst circuits, storms'!F40 | Credits, worst circuits, storms'!G25 | Credits, worst circuits, storms'!G26 | Credits, worst circuits, storms'!G27 | Credits, worst circuits, storms'!G28 | Credits, worst circuits, storms'!G29 | Credits, worst circuits, storms'!G30 | Credits, worst circuits, storms'!G31 | Credits, worst circuits, storms'!G32 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!G33 | Credits, worst circuits, storms'!G34 | Credits, worst circuits, storms'!G35 | Credits, worst circuits, storms'!G36 | Credits, worst circuits, storms'!G37 | Credits, worst circuits, storms'!G38 | Credits, worst circuits, storms'!G39 | Credits, worst circuits, storms'!G40 | Credits, worst circuits, storms'!H25 | Credits, worst circuits, storms'!H26 | Credits, worst circuits, storms'!H27 | Credits, worst circuits, storms'!H28 | Credits, worst circuits, storms'!H29 | Credits, worst circuits, storms'!H30 | Credits, worst circuits, storms'!H31 | Credits, worst circuits, storms'!H32 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!H33 | Credits, worst circuits, storms'!H34 | Credits, worst circuits, storms'!H35 | Credits, worst circuits, storms'!H36 | Credits, worst circuits, storms'!H37 | Credits, worst circuits, storms'!H38 | Credits, worst circuits, storms'!H39 | Credits, worst circuits, storms'!H40 | Credits, worst circuits, storms'!I25 | Credits, worst circuits, storms'!I26 | Credits, worst circuits, storms'!I27 | Credits, worst circuits, storms'!I28 | Credits, worst circuits, storms'!I29 | Credits, worst circuits, storms'!I30 | Credits, worst circuits, storms'!I31 | Credits, worst circuits, storms'!I32 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!I33 | Credits, worst circuits, storms'!I34 | Credits, worst circuits, storms'!I35 | Credits, worst circuits, storms'!I36 | Credits, worst circuits, storms'!I37 | Credits, worst circuits, storms'!I38 | Credits, worst circuits, storms'!I39 | Credits, worst circuits, storms'!I40 | Credits, worst circuits, storms'!J25 | Credits, worst circuits, storms'!J26 | Credits, worst circuits, storms'!J27 | Credits, worst circuits, storms'!J28 | Credits, worst circuits, storms'!J29 | Credits, worst circuits, storms'!J30 | Credits, worst circuits, storms'!J31 | Credits, worst circuits, storms'!J32 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!J33 | Credits, worst circuits, storms'!J34 | Credits, worst circuits, storms'!J35 | Credits, worst circuits, storms'!J36 | Credits, worst circuits, storms'!J37 | Credits, worst circuits, storms'!J38 | Credits, worst circuits, storms'!J39 | Credits, worst circuits, storms'!J40 | Credits, worst circuits, storms'!K25 | Credits, worst circuits, storms'!K26 | Credits, worst circuits, storms'!K27 | Credits, worst circuits, storms'!K28 | Credits, worst circuits, storms'!K29 | Credits, worst circuits, storms'!K30 | Credits, worst circuits, storms'!K31 | Credits, worst circuits, storms'!K32 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!K33 | Credits, worst circuits, storms'!K34 | Credits, worst circuits, storms'!K35 | Credits, worst circuits, storms'!K36 | Credits, worst circuits, storms'!K37 | Credits, worst circuits, storms'!K38 | Credits, worst circuits, storms'!K39 | Credits, worst circuits, storms'!K40 | Credits, worst circuits, storms'!L25 | Credits, worst circuits, storms'!L26 | Credits, worst circuits, storms'!L27 | Credits, worst circuits, storms'!L28 | Credits, worst circuits, storms'!L29 | Credits, worst circuits, storms'!L30 | Credits, worst circuits, storms'!L31 | Credits, worst circuits, storms'!L32 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!L33 | Credits, worst circuits, storms'!L34 | Credits, worst circuits, storms'!L35 | Credits, worst circuits, storms'!L36 | Credits, worst circuits, storms'!L37 | Credits, worst circuits, storms'!L38 | Credits, worst circuits, storms'!L39 | Credits, worst circuits, storms'!L40 | Credits, worst circuits, storms'!M25 | Credits, worst circuits, storms'!M26 | Credits, worst circuits, storms'!M27 | Credits, worst circuits, storms'!M28 | Credits, worst circuits, storms'!M29 | Credits, worst circuits, storms'!M30 | Credits, worst circuits, storms'!M31 | Credits, worst circuits, storms'!M32 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!M33 | Credits, worst circuits, storms'!M34 | Credits, worst circuits, storms'!M35 | Credits, worst circuits, storms'!M36 | Credits, worst circuits, storms'!M37 | Credits, worst circuits, storms'!M38 | Credits, worst circuits, storms'!M39 | Credits, worst circuits, storms'!M40
Title | Utility | Reporting_Period | C1_SAIFI_I-A | C1_SAIFI_CName | C1_SAIFI_CNum | C1_SAIFI_MCL | C1_SAIFI_M_W_R | C1_SAIFI_M_W_C | C1_SAIFI_M_W_I | C1_SAIFI_M_W_O | C1_SAIFI_A_ExMED_R | C1_SAIFI_A_ExMED_C | C1_SAIFI_A_ExMED_I | C1_SAIFI_A_ExMED_O | C1_SAIFI_CS_R | C1_SAIFI_CS_C | C1_SAIFI_CS_I | C1_SAIFI_Sub_Name | C1_SAIFI_S_ZC | C1_SAIFI_S_CT | C1_SAIFI_LCT | C1_SAIFI_LOC | C2_SAIFI_I-A | C2_SAIFI_CName | C2_SAIFI_CNum | C2_SAIFI_MCL | C2_SAIFI_M_W_R | C2_SAIFI_M_W_C | C2_SAIFI_M_W_I | C2_SAIFI_M_W_O | C2_SAIFI_A_ExMED_R | C2_SAIFI_A_ExMED_C | C2_SAIFI_A_ExMED_I | C2_SAIFI_A_ExMED_O | C2_SAIFI_CS_R | C2_SAIFI_CS_C | C2_SAIFI_CS_I | C2_SAIFI_Sub_Name | C2_SAIFI_S_ZC | C2_SAIFI_S_CT | C2_SAIFI_LCT | C2_SAIFI_LOC | C3_SAIFI_I-A | C3_SAIFI_CName | C3_SAIFI_CNum | C3_SAIFI_MCL | C3_SAIFI_M_W_R | C3_SAIFI_M_W_C | C3_SAIFI_M_W_I | C3_SAIFI_M_W_O | C3_SAIFI_A_ExMED_R | C3_SAIFI_A_ExMED_C | C3_SAIFI_A_ExMED_I | C3_SAIFI_A_ExMED_O | C3_SAIFI_CS_R | C3_SAIFI_CS_C | C3_SAIFI_CS_I | C3_SAIFI_Sub_Name | C3_SAIFI_S_ZC | C3_SAIFI_S_CT | C3_SAIFI_LCT | C3_SAIFI_LOC | C4_SAIFI_I-A | C4_SAIFI_CName | C4_SAIFI_CNum | C4_SAIFI_MCL | C4_SAIFI_M_W_R | C4_SAIFI_M_W_C | C4_SAIFI_M_W_I | C4_SAIFI_M_W_O | C4_SAIFI_A_ExMED_R | C4_SAIFI_A_ExMED_C | C4_SAIFI_A_ExMED_I | C4_SAIFI_A_ExMED_O | C4_SAIFI_CS_R | C4_SAIFI_CS_C | C4_SAIFI_CS_I | C4_SAIFI_Sub_Name | C4_SAIFI_S_ZC | C4_SAIFI_S_CT | C4_SAIFI_LCT | C4_SAIFI_LOC | C5_SAIFI_I-A | C5_SAIFI_CName | C5_SAIFI_CNum | C5_SAIFI_MCL | C5_SAIFI_M_W_R | C5_SAIFI_M_W_C | C5_SAIFI_M_W_I | C5_SAIFI_M_W_O | C5_SAIFI_A_ExMED_R | C5_SAIFI_A_ExMED_C | C5_SAIFI_A_ExMED_I | C5_SAIFI_A_ExMED_O | C5_SAIFI_CS_R | C5_SAIFI_CS_C | C5_SAIFI_CS_I | C5_SAIFI_Sub_Name | C5_SAIFI_S_ZC | C5_SAIFI_S_CT | C5_SAIFI_LCT | C5_SAIFI_LOC | C6_SAIFI_I-A | C6_SAIFI_CName | C6_SAIFI_CNum | C6_SAIFI_MCL | C6_SAIFI_M_W_R | C6_SAIFI_M_W_C | C6_SAIFI_M_W_I | C6_SAIFI_M_W_O | C6_SAIFI_A_ExMED_R | C6_SAIFI_A_ExMED_C | C6_SAIFI_A_ExMED_I | C6_SAIFI_A_ExMED_O | C6_SAIFI_CS_R | C6_SAIFI_CS_C | C6_SAIFI_CS_I | C6_SAIFI_Sub_Name | C6_SAIFI_S_ZC | C6_SAIFI_S_CT | C6_SAIFI_LCT | C6_SAIFI_LOC | C7_SAIFI_I-A | C7_SAIFI_CName | C7_SAIFI_CNum | C7_SAIFI_MCL | C7_SAIFI_M_W_R | C7_SAIFI_M_W_C | C7_SAIFI_M_W_I | C7_SAIFI_M_W_O | C7_SAIFI_A_ExMED_R | C7_SAIFI_A_ExMED_C | C7_SAIFI_A_ExMED_I | C7_SAIFI_A_ExMED_O | C7_SAIFI_CS_R | C7_SAIFI_CS_C | C7_SAIFI_CS_I | C7_SAIFI_Sub_Name | C7_SAIFI_S_ZC | C7_SAIFI_S_CT | C7_SAIFI_LCT | C7_SAIFI_LOC | C8_SAIFI_I-A | C8_SAIFI_CName | C8_SAIFI_CNum | C8_SAIFI_MCL | C8_SAIFI_M_W_R | C8_SAIFI_M_W_C | C8_SAIFI_M_W_I | C8_SAIFI_M_W_O | C8_SAIFI_A_ExMED_R | C8_SAIFI_A_ExMED_C | C8_SAIFI_A_ExMED_I | C8_SAIFI_A_ExMED_O | C8_SAIFI_CS_R | C8_SAIFI_CS_C | C8_SAIFI_CS_I | C8_SAIFI_Sub_Name | C8_SAIFI_S_ZC | C8_SAIFI_S_CT | C8_SAIFI_LCT | C8_SAIFI_LOC | C9_SAIFI_I-A | C9_SAIFI_CName | C9_SAIFI_CNum | C9_SAIFI_MCL | C9_SAIFI_M_W_R | C9_SAIFI_M_W_C | C9_SAIFI_M_W_I | C9_SAIFI_M_W_O | C9_SAIFI_A_ExMED_R | C9_SAIFI_A_ExMED_C | C9_SAIFI_A_ExMED_I | C9_SAIFI_A_ExMED_O | C9_SAIFI_CS_R | C9_SAIFI_CS_C | C9_SAIFI_CS_I | C9_SAIFI_Sub_Name | C9_SAIFI_S_ZC | C9_SAIFI_S_CT | C9_SAIFI_LCT | C9_SAIFI_LOC | C10_SAIFI_I-A | C10_SAIFI_CName | C10_SAIFI_CNum | C10_SAIFI_MCL | C10_SAIFI_M_W_R | C10_SAIFI_M_W_C | C10_SAIFI_M_W_I | C10_SAIFI_M_W_O | C10_SAIFI_A_ExMED_R | C10_SAIFI_A_ExMED_C | C10_SAIFI_A_ExMED_I | C10_SAIFI_A_ExMED_O | C10_SAIFI_CS_R | C10_SAIFI_CS_C | C10_SAIFI_CS_I | C10_SAIFI_Sub_Name | C10_SAIFI_S_ZC | C10_SAIFI_S_CT | C10_SAIFI_LCT | C10_SAIFI_LOC
U-21122 Response Data | Consumers Energy Co. | 45046 | circuit1 | OXBOW | 123102 | 34.1 | 2.37745 | 0.19608 | 0 | 2.64706 |  |  |  |  | 817 | 90 | 0 | BIG PRAIRIE | 49337, 49349 | 26123970700, 26123970800 | 43646 | Trees - Outside ROW-99.8%, Trees-0.1%, Equipment Failure-0.1% | circuit2 | PARKER | 46501 | 10.85 | 2.44832 | 0.12532 | 0 | 2.57881 |  |  |  |  | 708 | 149 | 3 | DIVISION | 49315, 49508, 49548 | 26081014602, 26081014701, 26081014704, 26081014803, 26081014805 | 34515 | Weather-99.9%, Animal-0.1% | circuit3 | ADDISON | 18302 | 61.02 | 1.89163 | 0.3202 | 0.00493 | 2.22906 |  |  |  |  | 741 | 128 | 2 | MANITOU BEACH | 49220, 49233, 49247, 49249, 49253, 49262, 49271 | 26059050100, 26059050600, 26091060401, 26091060402 | 43281 | Animal-86.0%, Forced Outage/Emergency-12.2%, No Specific Cause Found-1.5%, Equipment Failure-0.1%, Unique Incident-0.1%, Public Damage-0.1% | circuit4 | BONANZA | 43503 | 25.25 | 1.71845 | 0.19417 | 0 | 1.93204 |  |  |  |  | 189 | 23 | 0 | LAKE ODESSA | 48849, 49325 | 26015010100, 26015010200, 26067031200, 26067031300 | 40359 | Car/Pole Accident-100.0% | circuit5 | BURROWS | 33902 | 7.57 | 1.83095 | 0.08571 | 0 | 1.92619 |  |  |  |  | 998 | 41 | 0 | BURROWS | 48602, 48638 | 26145001400, 26145010501, 26145010600 | 44742 | No Specific Cause Found-100.0% | circuit6 | GRATIOT | 33903 | 16.85 | 1.83838 | 0.06612 | 0 | 1.91644 |  |  |  |  | 2255 | 81 | 0 | BURROWS | 48602, 48638 | 26145001300, 26145001400, 26145002100, 26145010402, 26145010501 | 44742 | No Specific Cause Found-100.0% | circuit7 | ELK RAPIDS | 79802 | 26.24 | 1.52221 | 0.38089 | 0.00135 | 1.91521 |  |  |  |  | 1234 | 322 | 1 | ANTRIM | 49629, 49648, 49690 | 26009960600 | 42551 | No Specific Cause Found-99.9%, Equipment Failure-0.1% | circuit8 | HUBBARD LAKE | 151601 | 15.54 | 1.59611 | 0.15335 | 0.00216 | 1.76026 |  |  |  |  | 444 | 49 | 1 | HUBBARD LAKE | 48705, 48742, 48762 | 26001000100, 26001970400, 26001970500 | 43281 | Trees-51.9%, Equipment Failure-48.1% | circuit9 | STOREY ROAD | 45301 | 82.87 | 1.50214 | 0.1826 | 0 | 1.6933 |  |  |  |  | 1262 | 211 | 2 | BRICKER | 48809, 48838, 49331, 49341 | 26067030300, 26067030400, 26081010802, 26081010902, 26117971100, 26117971300 | 44012 | No Specific Cause Found-63.8%, Equipment Failure-36.1%, Unique Incident-0.1% | circuit10 | RURAL | 37902 | 127.93 | 1.45994 | 0.17719 | 0 | 1.64185 |  |  |  |  | 1025 | 136 | 0 | HESPERIA | 49309, 49349, 49412, 49421 | 26123970100, 26123970300, 26123970400, 26123970600, 26127010500, 26127010600 | 40359 | Trees-64.2%, Equipment Failure-35.7%, Weather-0.1%
Title | Utility | Reporting_Period | C1_SAIFI_I-A | C1_SAIFI_CName | C1_SAIFI_CNum | C1_SAIFI_MCL | C1_SAIFI_M_W_R | C1_SAIFI_M_W_C | C1_SAIFI_M_W_I | C1_SAIFI_M_W_O | C1_SAIFI_A_ExMED_R | C1_SAIFI_A_ExMED_C | C1_SAIFI_A_ExMED_I | C1_SAIFI_A_ExMED_O | C1_SAIFI_CS_R | C1_SAIFI_CS_C | C1_SAIFI_CS_I | C1_SAIFI_Sub_Name | C1_SAIFI_S_ZC | C1_SAIFI_S_CT | C1_SAIFI_LCT | C1_SAIFI_LOC | C2_SAIFI_I-A | C2_SAIFI_CName | C2_SAIFI_CNum | C2_SAIFI_MCL | C2_SAIFI_M_W_R | C2_SAIFI_M_W_C | C2_SAIFI_M_W_I | C2_SAIFI_M_W_O | C2_SAIFI_A_ExMED_R | C2_SAIFI_A_ExMED_C | C2_SAIFI_A_ExMED_I | C2_SAIFI_A_ExMED_O | C2_SAIFI_CS_R | C2_SAIFI_CS_C | C2_SAIFI_CS_I | C2_SAIFI_Sub_Name | C2_SAIFI_S_ZC | C2_SAIFI_S_CT | C2_SAIFI_LCT | C2_SAIFI_LOC | C3_SAIFI_I-A | C3_SAIFI_CName | C3_SAIFI_CNum | C3_SAIFI_MCL | C3_SAIFI_M_W_R | C3_SAIFI_M_W_C | C3_SAIFI_M_W_I | C3_SAIFI_M_W_O | C3_SAIFI_A_ExMED_R | C3_SAIFI_A_ExMED_C | C3_SAIFI_A_ExMED_I | C3_SAIFI_A_ExMED_O | C3_SAIFI_CS_R | C3_SAIFI_CS_C | C3_SAIFI_CS_I | C3_SAIFI_Sub_Name | C3_SAIFI_S_ZC | C3_SAIFI_S_CT | C3_SAIFI_LCT | C3_SAIFI_LOC | C4_SAIFI_I-A | C4_SAIFI_CName | C4_SAIFI_CNum | C4_SAIFI_MCL | C4_SAIFI_M_W_R | C4_SAIFI_M_W_C | C4_SAIFI_M_W_I | C4_SAIFI_M_W_O | C4_SAIFI_A_ExMED_R | C4_SAIFI_A_ExMED_C | C4_SAIFI_A_ExMED_I | C4_SAIFI_A_ExMED_O | C4_SAIFI_CS_R | C4_SAIFI_CS_C | C4_SAIFI_CS_I | C4_SAIFI_Sub_Name | C4_SAIFI_S_ZC | C4_SAIFI_S_CT | C4_SAIFI_LCT | C4_SAIFI_LOC | C5_SAIFI_I-A | C5_SAIFI_CName | C5_SAIFI_CNum | C5_SAIFI_MCL | C5_SAIFI_M_W_R | C5_SAIFI_M_W_C | C5_SAIFI_M_W_I | C5_SAIFI_M_W_O | C5_SAIFI_A_ExMED_R | C5_SAIFI_A_ExMED_C | C5_SAIFI_A_ExMED_I | C5_SAIFI_A_ExMED_O | C5_SAIFI_CS_R | C5_SAIFI_CS_C | C5_SAIFI_CS_I | C5_SAIFI_Sub_Name | C5_SAIFI_S_ZC | C5_SAIFI_S_CT | C5_SAIFI_LCT | C5_SAIFI_LOC | C6_SAIFI_I-A | C6_SAIFI_CName | C6_SAIFI_CNum | C6_SAIFI_MCL | C6_SAIFI_M_W_R | C6_SAIFI_M_W_C | C6_SAIFI_M_W_I | C6_SAIFI_M_W_O | C6_SAIFI_A_ExMED_R | C6_SAIFI_A_ExMED_C | C6_SAIFI_A_ExMED_I | C6_SAIFI_A_ExMED_O | C6_SAIFI_CS_R | C6_SAIFI_CS_C | C6_SAIFI_CS_I | C6_SAIFI_Sub_Name | C6_SAIFI_S_ZC | C6_SAIFI_S_CT | C6_SAIFI_LCT | C6_SAIFI_LOC | C7_SAIFI_I-A | C7_SAIFI_CName | C7_SAIFI_CNum | C7_SAIFI_MCL | C7_SAIFI_M_W_R | C7_SAIFI_M_W_C | C7_SAIFI_M_W_I | C7_SAIFI_M_W_O | C7_SAIFI_A_ExMED_R | C7_SAIFI_A_ExMED_C | C7_SAIFI_A_ExMED_I | C7_SAIFI_A_ExMED_O | C7_SAIFI_CS_R | C7_SAIFI_CS_C | C7_SAIFI_CS_I | C7_SAIFI_Sub_Name | C7_SAIFI_S_ZC | C7_SAIFI_S_CT | C7_SAIFI_LCT | C7_SAIFI_LOC | C8_SAIFI_I-A | C8_SAIFI_CName | C8_SAIFI_CNum | C8_SAIFI_MCL | C8_SAIFI_M_W_R | C8_SAIFI_M_W_C | C8_SAIFI_M_W_I | C8_SAIFI_M_W_O | C8_SAIFI_A_ExMED_R | C8_SAIFI_A_ExMED_C | C8_SAIFI_A_ExMED_I | C8_SAIFI_A_ExMED_O | C8_SAIFI_CS_R | C8_SAIFI_CS_C | C8_SAIFI_CS_I | C8_SAIFI_Sub_Name | C8_SAIFI_S_ZC | C8_SAIFI_S_CT | C8_SAIFI_LCT | C8_SAIFI_LOC | C9_SAIFI_I-A | C9_SAIFI_CName | C9_SAIFI_CNum | C9_SAIFI_MCL | C9_SAIFI_M_W_R | C9_SAIFI_M_W_C | C9_SAIFI_M_W_I | C9_SAIFI_M_W_O | C9_SAIFI_A_ExMED_R | C9_SAIFI_A_ExMED_C | C9_SAIFI_A_ExMED_I | C9_SAIFI_A_ExMED_O | C9_SAIFI_CS_R | C9_SAIFI_CS_C | C9_SAIFI_CS_I | C9_SAIFI_Sub_Name | C9_SAIFI_S_ZC | C9_SAIFI_S_CT | C9_SAIFI_LCT | C9_SAIFI_LOC | C10_SAIFI_I-A | C10_SAIFI_CName | C10_SAIFI_CNum | C10_SAIFI_MCL | C10_SAIFI_M_W_R | C10_SAIFI_M_W_C | C10_SAIFI_M_W_I | C10_SAIFI_M_W_O | C10_SAIFI_A_ExMED_R | C10_SAIFI_A_ExMED_C | C10_SAIFI_A_ExMED_I | C10_SAIFI_A_ExMED_O | C10_SAIFI_CS_R | C10_SAIFI_CS_C | C10_SAIFI_CS_I | C10_SAIFI_Sub_Name | C10_SAIFI_S_ZC | C10_SAIFI_S_CT | C10_SAIFI_LCT | C10_SAIFI_LOC
Linked | Consumers Energy Co. | 2023-04-30 | circuit1 | OXBOW | 123102 | 34.1 | 2.3775 | 0.19608 | 0 | 2.6471 | #REF! | #REF! | #REF! | #REF! | 817 | 90 | 0 | BIG PRAIRIE | 49337, 49349 | 26123970700, 26123970800 | 2019-06-30 | Trees - Outside ROW-99.8%, Trees-0.1%, Equipment Failure-0.1% | circuit2 | PARKER | 46501 | 10.85 | 2.4483 | 0.12532 | 0 | 2.5788 | #REF! | #REF! | #REF! | #REF! | 708 | 149 | 3 | DIVISION | 49315, 49508, 49548 | 26081014602, 26081014701, 26081014704, 26081014803, 26081014805 | 1994-06-30 | Weather-99.9%, Animal-0.1% | circuit3 | ADDISON | 18302 | 61.02 | 1.8916 | 0.3202 | 0.00493 | 2.2291 | #REF! | #REF! | #REF! | #REF! | 741 | 128 | 2 | MANITOU BEACH | 49220, 49233, 49247, 49249, 49253, 49262, 49271 | 26059050100, 26059050600, 26091060401, 26091060402 | 2018-06-30 | Animal-86.0%, Forced Outage/Emergency-12.2%, No Specific Cause Found-1.5%, Equipment Failure-0.1%, Unique Incident-0.1%, Public Damage-0.1% | circuit4 | BONANZA | 43503 | 25.25 | 1.7185 | 0.19417 | 0 | 1.932 | #REF! | #REF! | #REF! | #REF! | 189 | 23 | 0 | LAKE ODESSA | 48849, 49325 | 26015010100, 26015010200, 26067031200, 26067031300 | 2010-06-30 | Car/Pole Accident-100.0% | circuit5 | BURROWS | 33902 | 7.57 | 1.831 | 0.08571 | 0 | 1.9262 | #REF! | #REF! | #REF! | #REF! | 998 | 41 | 0 | BURROWS | 48602, 48638 | 26145001400, 26145010501, 26145010600 | 2022-06-30 | No Specific Cause Found-100.0% | circuit6 | GRATIOT | 33903 | 16.85 | 1.8384 | 0.06612 | 0 | 1.9164 | #REF! | #REF! | #REF! | #REF! | 2255 | 81 | 0 | BURROWS | 48602, 48638 | 26145001300, 26145001400, 26145002100, 26145010402, 26145010501 | 2022-06-30 | No Specific Cause Found-100.0% | circuit7 | ELK RAPIDS | 79802 | 26.24 | 1.5222 | 0.38089 | 0.00135 | 1.9152 | #REF! | #REF! | #REF! | #REF! | 1234 | 322 | 1 | ANTRIM | 49629, 49648, 49690 | 26009960600 | 2016-06-30 | No Specific Cause Found-99.9%, Equipment Failure-0.1% | circuit8 | HUBBARD LAKE | 151601 | 15.54 | 1.5961 | 0.15335 | 0.00216 | 1.7603 | #REF! | #REF! | #REF! | #REF! | 444 | 49 | 1 | HUBBARD LAKE | 48705, 48742, 48762 | 26001000100, 26001970400, 26001970500 | 2018-06-30 | Trees-51.9%, Equipment Failure-48.1% | circuit9 | STOREY ROAD | 45301 | 82.87 | 1.5021 | 0.1826 | 0 | 1.6933 | #REF! | #REF! | #REF! | #REF! | 1262 | 211 | 2 | BRICKER | 48809, 48838, 49331, 49341 | 26067030300, 26067030400, 26081010802, 26081010902, 26117971100, 26117971300 | 2020-06-30 | No Specific Cause Found-63.8%, Equipment Failure-36.1%, Unique Incident-0.1% | circuit10 | RURAL | 37902 | 127.93 | 1.4599 | 0.17719 | 0 | 1.6419 | #REF! | #REF! | #REF! | #REF! | 1025 | 136 | 0 | HESPERIA | 49309, 49349, 49412, 49421 | 26123970100, 26123970300, 26123970400, 26123970600, 26127010500, 26127010600 | 2010-06-30 | Trees-64.2%, Equipment Failure-35.7%, Weather-0.1%
Static | Credits, worst circuits, storms'!C3 | Credits, worst circuits, storms'!C4 | Credits, worst circuits, storms'!D42 | Credits, worst circuits, storms'!D43 | Credits, worst circuits, storms'!D44 | Credits, worst circuits, storms'!D45 | Credits, worst circuits, storms'!D46 | Credits, worst circuits, storms'!D47 | Credits, worst circuits, storms'!D48 | Credits, worst circuits, storms'!D49 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!D50 | Credits, worst circuits, storms'!D51 | Credits, worst circuits, storms'!D52 | Credits, worst circuits, storms'!D53 | Credits, worst circuits, storms'!D54 | Credits, worst circuits, storms'!D55 | Credits, worst circuits, storms'!D56 | Credits, worst circuits, storms'!D57 | Credits, worst circuits, storms'!E42 | Credits, worst circuits, storms'!E43 | Credits, worst circuits, storms'!E44 | Credits, worst circuits, storms'!E45 | Credits, worst circuits, storms'!E46 | Credits, worst circuits, storms'!E47 | Credits, worst circuits, storms'!E48 | Credits, worst circuits, storms'!E49 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!E50 | Credits, worst circuits, storms'!E51 | Credits, worst circuits, storms'!E52 | Credits, worst circuits, storms'!E53 | Credits, worst circuits, storms'!E54 | Credits, worst circuits, storms'!E55 | Credits, worst circuits, storms'!E56 | Credits, worst circuits, storms'!E57 | Credits, worst circuits, storms'!F42 | Credits, worst circuits, storms'!F43 | Credits, worst circuits, storms'!F44 | Credits, worst circuits, storms'!F45 | Credits, worst circuits, storms'!F46 | Credits, worst circuits, storms'!F47 | Credits, worst circuits, storms'!F48 | Credits, worst circuits, storms'!F49 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!F50 | Credits, worst circuits, storms'!F51 | Credits, worst circuits, storms'!F52 | Credits, worst circuits, storms'!F53 | Credits, worst circuits, storms'!F54 | Credits, worst circuits, storms'!F55 | Credits, worst circuits, storms'!F56 | Credits, worst circuits, storms'!F57 | Credits, worst circuits, storms'!G42 | Credits, worst circuits, storms'!G43 | Credits, worst circuits, storms'!G44 | Credits, worst circuits, storms'!G45 | Credits, worst circuits, storms'!G46 | Credits, worst circuits, storms'!G47 | Credits, worst circuits, storms'!G48 | Credits, worst circuits, storms'!G49 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!G50 | Credits, worst circuits, storms'!G51 | Credits, worst circuits, storms'!G52 | Credits, worst circuits, storms'!G53 | Credits, worst circuits, storms'!G54 | Credits, worst circuits, storms'!G55 | Credits, worst circuits, storms'!G56 | Credits, worst circuits, storms'!G57 | Credits, worst circuits, storms'!H42 | Credits, worst circuits, storms'!H43 | Credits, worst circuits, storms'!H44 | Credits, worst circuits, storms'!H45 | Credits, worst circuits, storms'!H46 | Credits, worst circuits, storms'!H47 | Credits, worst circuits, storms'!H48 | Credits, worst circuits, storms'!H49 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!H50 | Credits, worst circuits, storms'!H51 | Credits, worst circuits, storms'!H52 | Credits, worst circuits, storms'!H53 | Credits, worst circuits, storms'!H54 | Credits, worst circuits, storms'!H55 | Credits, worst circuits, storms'!H56 | Credits, worst circuits, storms'!H57 | Credits, worst circuits, storms'!I42 | Credits, worst circuits, storms'!I43 | Credits, worst circuits, storms'!I44 | Credits, worst circuits, storms'!I45 | Credits, worst circuits, storms'!I46 | Credits, worst circuits, storms'!I47 | Credits, worst circuits, storms'!I48 | Credits, worst circuits, storms'!I49 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!I50 | Credits, worst circuits, storms'!I51 | Credits, worst circuits, storms'!I52 | Credits, worst circuits, storms'!I53 | Credits, worst circuits, storms'!I54 | Credits, worst circuits, storms'!I55 | Credits, worst circuits, storms'!I56 | Credits, worst circuits, storms'!I57 | Credits, worst circuits, storms'!J42 | Credits, worst circuits, storms'!J43 | Credits, worst circuits, storms'!J44 | Credits, worst circuits, storms'!J45 | Credits, worst circuits, storms'!J46 | Credits, worst circuits, storms'!J47 | Credits, worst circuits, storms'!J48 | Credits, worst circuits, storms'!J49 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!J50 | Credits, worst circuits, storms'!J51 | Credits, worst circuits, storms'!J52 | Credits, worst circuits, storms'!J53 | Credits, worst circuits, storms'!J54 | Credits, worst circuits, storms'!J55 | Credits, worst circuits, storms'!J56 | Credits, worst circuits, storms'!J57 | Credits, worst circuits, storms'!K42 | Credits, worst circuits, storms'!K43 | Credits, worst circuits, storms'!K44 | Credits, worst circuits, storms'!K45 | Credits, worst circuits, storms'!K46 | Credits, worst circuits, storms'!K47 | Credits, worst circuits, storms'!K48 | Credits, worst circuits, storms'!K49 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!K50 | Credits, worst circuits, storms'!K51 | Credits, worst circuits, storms'!K52 | Credits, worst circuits, storms'!K53 | Credits, worst circuits, storms'!K54 | Credits, worst circuits, storms'!K55 | Credits, worst circuits, storms'!K56 | Credits, worst circuits, storms'!K57 | Credits, worst circuits, storms'!L42 | Credits, worst circuits, storms'!L43 | Credits, worst circuits, storms'!L44 | Credits, worst circuits, storms'!L45 | Credits, worst circuits, storms'!L46 | Credits, worst circuits, storms'!L47 | Credits, worst circuits, storms'!L48 | Credits, worst circuits, storms'!L49 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!L50 | Credits, worst circuits, storms'!L51 | Credits, worst circuits, storms'!L52 | Credits, worst circuits, storms'!L53 | Credits, worst circuits, storms'!L54 | Credits, worst circuits, storms'!L55 | Credits, worst circuits, storms'!L56 | Credits, worst circuits, storms'!L57 | Credits, worst circuits, storms'!M42 | Credits, worst circuits, storms'!M43 | Credits, worst circuits, storms'!M44 | Credits, worst circuits, storms'!M45 | Credits, worst circuits, storms'!M46 | Credits, worst circuits, storms'!M47 | Credits, worst circuits, storms'!M48 | Credits, worst circuits, storms'!M49 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | NormalizedData'!EW1 | Credits, worst circuits, storms'!M50 | Credits, worst circuits, storms'!M51 | Credits, worst circuits, storms'!M52 | Credits, worst circuits, storms'!M53 | Credits, worst circuits, storms'!M54 | Credits, worst circuits, storms'!M55 | Credits, worst circuits, storms'!M56 | Credits, worst circuits, storms'!M57
Title | Utility | Reporting_Period | M_MRF | M_NSI | M_WDRF_120 | M_WDRF_180 | M_Rest_A | M_Rest_N | M_Rest_GS | M_Rest_CC | M_CEMI4 | M_LCTT_A_MI | M_LCTT_Cap_Spend | M_LCTT_OM_Spend | M_LCTT_QLCT_MI | M_LCTT_T_Percent | M_LCTT_C_Percent | M_TCO | M_OC_Eq | M_OC_Ltn | M_OC_Plan | M_OC_PS | M_OC_Pub | M_OC_Veg | M_OC_Weather | M_OC_Wild | M_OC_Unk | M_OC_O | M_SAIDI | M_SAIFI | M_CAIDI | M_ASAI | M_MAIFI | YTD_MRF | YTD_NSI | YTD_WDRF_120 | YTD_WDRF_180 | YTD_Rest_A | YTD_Rest_N | YTD_Rest_GS | YTD_Rest_CC | YTD_CEMI4 | YTD_LCTT_A_MI | YTD_LCTT_Cap_Spend | YTD_LCTT_OM_Spend | YTD_LCTT_QLCT_MI | YTD_LCTT_T_Percent | YTD_LCTT_C_Percent | YTD_TCO | YTD_OC_Eq | YTD_OC_Ltn | YTD_OC_Plan | YTD_OC_PS | YTD_OC_Pub | YTD_OC_Veg | YTD_OC_Weather | YTD_OC_Wild | YTD_OC_Unk | YTD_OC_O | YTD_SAIDI | YTD_SAIFI | YTD_CAIDI | YTD_ASAI | YTD_MAIFI
U-21122 Response Data | Consumers Energy Co. | 2023-04-30 | 0.938 | 0.578 | 0.809 | 0.877 | 1 | 0.918 | 0.999 |  | 29662 | 492.267778003351 | 475 | 7850 | 1332.7918213752 | 0.369350839424736 | 0.679120953796013 | 166479 | 36069 | 10596 | 19857 | 4278 | 7166 | 42075 | 15248 | 3117 | 19055 | 9018 | 13.82 | 0.08 | 181.67 | 0.9997 | 0.1849 | 0.935 | 0.4818 | 0.501 | 0.617 | 0.83 | 0.953 | 0.982 | 0.733 | 29662 | 1792.39837907834 | 1638 | 27842 | 2639.2918213752 | 0.679120953796013 | 0.679120953796013 | 949597 | 137142 | 11281 | 38039 | 7652 | 54190 | 379590 | 198188 | 9142 | 63179 | 51194 | 497.58 | 0.48 | 1033.97 | 0.9971 | 0.7827
Title | Utility | Reporting_Period | M_MRF | M_NSI | M_WDRF_120 | M_WDRF_180 | M_Rest_A | M_Rest_N | M_Rest_GS | M_Rest_CC | M_CEMI4 | M_LCTT_A_MI | M_LCTT_Cap_Spend | M_LCTT_OM_Spend | M_LCTT_QLCT_MI | M_LCTT_T_Percent | M_LCTT_C_Percent | M_TCO | M_OC_Eq | M_OC_Ltn | M_OC_Plan | M_OC_PS | M_OC_Pub | M_OC_Veg | M_OC_Weather | M_OC_Wild | M_OC_Unk | M_OC_O | M_SAIDI | M_SAIFI | M_CAIDI | M_ASAI | M_MAIFI | YTD_MRF | YTD_NSI | YTD_WDRF_120 | YTD_WDRF_180 | YTD_Rest_A | YTD_Rest_N | YTD_Rest_GS | YTD_Rest_CC | YTD_CEMI4 | YTD_LCTT_A_MI | YTD_LCTT_Cap_Spend | YTD_LCTT_OM_Spend | YTD_LCTT_QLCT_MI | YTD_LCTT_T_Percent | YTD_LCTT_C_Percent | YTD_TCO | YTD_OC_Eq | YTD_OC_Ltn | YTD_OC_Plan | YTD_OC_PS | YTD_OC_Pub | YTD_OC_Veg | YTD_OC_Weather | YTD_OC_Wild | YTD_OC_Unk | YTD_OC_O | YTD_SAIDI | YTD_SAIFI | YTD_CAIDI | YTD_ASAI | YTD_MAIFI
Linked | Consumers Energy Co. | 2023-04-30 | 93.8% | 57.8% | 80.9% | 87.7% | 100% | 91.8% | 99.9% | 0% | 29662 | 492.2678 | 475 | 7850 | 1332.7918 | 36.94% | 67.91% | 166479 | 36069 | 10596 | 19857 | 4278 | 7166 | 42075 | 15248 | 3117 | 19055 | 9018 | 13.82 | 0.08 | 181.67 | 0.9997 | 18.49% | 93.5% | 48.18% | 50.1% | 61.7% | 83% | 95.3% | 98.2% | 0.733 | 29662 | 1792.3984 | 1638 | 27842 | 263929% | 67.91% | 0.67912 | 949597 | 137142 | 11281 | 38039 | 7652 | 54190 | 379590 | 198188 | 9142 | 63179 | 51194 | 497.58 | 0.48 | 1033.97 | 0.9971 | 0.7827
Static | System Reliability Data'!C3 | System Reliability Data'!C4 | System Reliability Data'!C11 | System Reliability Data'!D11 | System Reliability Data'!E11 | System Reliability Data'!F11 | System Reliability Data'!G11 | System Reliability Data'!H11 | System Reliability Data'!I11 | System Reliability Data'!J11 | System Reliability Data'!K11 | System Reliability Data'!L11 | System Reliability Data'!M11 | System Reliability Data'!N11 | System Reliability Data'!O11 | System Reliability Data'!P11 | System Reliability Data'!Q11 | System Reliability Data'!R11 | System Reliability Data'!S11 | System Reliability Data'!T11 | System Reliability Data'!U11 | System Reliability Data'!V11 | System Reliability Data'!W11 | System Reliability Data'!X11 | System Reliability Data'!Y11 | System Reliability Data'!Z11 | System Reliability Data'!AA11 | System Reliability Data'!AB11 | System Reliability Data'!AC11 | System Reliability Data'!AD11 | System Reliability Data'!AE11 | System Reliability Data'!AF11 | System Reliability Data'!AG11 | System Reliability Data'!C12 | System Reliability Data'!D12 | System Reliability Data'!E12 | System Reliability Data'!F12 | System Reliability Data'!G12 | System Reliability Data'!H12 | System Reliability Data'!I12 | System Reliability Data'!J12 | System Reliability Data'!K12 | System Reliability Data'!L12 | System Reliability Data'!M12 | System Reliability Data'!N12 | System Reliability Data'!O12 | System Reliability Data'!P12 | System Reliability Data'!Q12 | System Reliability Data'!R12 | System Reliability Data'!S12 | System Reliability Data'!T12 | System Reliability Data'!U12 | System Reliability Data'!V12 | System Reliability Data'!W12 | System Reliability Data'!X12 | System Reliability Data'!Y12 | System Reliability Data'!Z12 | System Reliability Data'!AA12 | System Reliability Data'!AB12 | System Reliability Data'!AC12 | System Reliability Data'!AD12 | System Reliability Data'!AE12 | System Reliability Data'!AF12 | System Reliability Data'!AG12